| Bureau of Labor Standards / OSHA – References: | NFPA #13 OSHA 1910.159 |
| --- | --- |
| Automatic Fire Sprinklers |  |
| Locations: | Throughout entire facility |
| Inspector: | The person inspecting the Sprinkler system shall be appointed by the CTE. Types of Systems Location of each Control Valves and gauges Fire Department connections Proper procedures for inspecting. |
| Frequency of Inspections: | Inspections should be conducted monthly and quarterly |
| Inspection: | See Attached Form |
| Training |  |

| Fire Sprinkler Inspection Form | YES | NO |
| --- | --- | --- |
| Monthly Inspection - Valves |
| In their normal open or closed position |  |  |
| Properly sealed, locked, or supervised |  |  |
| Accessible |  |  |
| Free from external leaks |  |  |
| Free of physical damage |  |  |
| Appropriately labeled |  |  |
| (Alarm Valves) Retarding chamber or alarm drains are not leaking |  |  |
| Monthly Inspection – Gauges- Wet System |
| Gauges shall be inspected monthly to ensure they are in good condition and that normal water supply pressure is being maintained. |  |  |
| Monthly Inspection – Gauges- Dry System |
| The gauge on the supply side of the dry pipe valve shall indicate that the normal supply water pressure is being maintained. |  |  |
| The gauge on the quick-opening device, if provided, shall indicate the same pressure as the gauge on the system side of the dry pipe valve. |  |  |
| Gauges on systems with low air or nitrogen pressure alarms shall be inspected monthly. |  |  |
| Quarterly Inspection |
| The Quarterly Inspection should include everything in the monthly inspection as well as the following: |  |  |
| Inspect water flow alarm and supervisory alarm devices for physical damage. |  |  |
| Inspect and test the water flow alarm by opening the test connection on a wet pipe system and the bypass connection on a dry pipe system. |  |  |
| If the sprinkler system is hydraulic, inspect the hydraulic nameplate to ensure that it’s attached and easily seen. |  |  |
| Inspect fire department connections to make sure they are visible and undamaged, and ensure that gaskets and valves are not leaking or damaged. |  |  |
| Inspect pressure reducing valves and relief valves, if provided, to verify the following: In the open position Not leaking Maintaining downstream pressures in accordance with the design criteria In good condition, with hand-wheels installed and unbroken. |  |  |