## System losses
MPS System Loss Factors
(These system losses exclude losses over PTF facilities)
Loss Factors by Voltage Level
|  |  | Winter | Non-winter | Annual
|  | Secondary | 0.91907 | 0.92345 | 0.92138
|  | Primary | 0.94876 | 0.95718 | 0.95323
|  | Sub-Transmission | 0.96336 | 0.97193 | 0.96757
|  | Transmission | 0.9782 | 0.9782 | 0.9782
Weighted Average Loss Factors by Class
(Based on 2015 Usage)
Residential/Small Non-residential Class |  |  |  | Total Class | SO Only
|  | % of Class @ Secondary Voltage |  | 100% | 100%
Small Class Weighted Average Loss Factor |  |  |  | 0.92138 | 0.92138
Medium Class |  |  |  | Total Class | SO Only
|  | % of Class @ Secondary Voltage |  | 88.3% | 90.9%
|  | % of Class @ Primary Voltage |  | 11.7% | 9.1%
|  |  |  | 100% | 100%
Medium Class Weighted Average Loss Factor |  |  |  | 0.92511 | 0.92428
Large Class |  |  |  | Total Class | SO Only
|  | % of Class @ Secondary |  | 6.86% | 0%
|  | % of Class @ Primary |  | 9.89% | 0%
|  | % of Class @ Sub-Transmission |  | 18.65% | 0%
|  | % of Class @ Transmission |  | 64.6% | 100%
|  |  |  | 100% | 100%
Large Class Weighted Average Loss Factor |  |  |  | 0.96985 | 0.9782
Application of Loss Factors
Total MWh to be provided = (MWh measured at meter) / (applicable loss factor)
Example: | Usage @ meter = 9,700 MWh
|  | (9,700) / (0.92138) | 10527.6867