02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

174		BOARD OF BOILERS AND PRESSURE VESSELS

# Chapter 13:	LOW PRESSURE BOILERS

SUMMARY: This Chapter establishes specific requirements for the identification, construction, installation, inspection, and operation of low pressure boilers. Consistent with 32 M.R.S.A. § 15102(1), the Board’s rules regulate only those heating boilers located in schoolhouses or owned by municipalities and includes remote central heating plants. This Chapter also establishes specific requirements for low pressure “process” boilers and water heaters with a heat input greater than 200,000 Btu/hour.

1.	Exceptions to this Chapter.

A.	Hot water heating boilers and hot water supply boilers are exempt from the certificate inspection process provided the following conditions are met:

- The boilers are constructed and installed in accordance with the Board rules and pass an initial installation inspection;

- The heat input to any one object is less than 200,000 Btu/hour; and

- The aggregate heat input of the plant is less than 300,000 Btu/hour.

  - Water heaters are exempt from the provisions of this Chapter provided the following conditions are met.

- The water heater is built and installed to a nationally recognized code;

(2)	The heat input is less than 200,000 Btu/hour;

(3)	A properly sized ASME/NB rated pressure relief device is installed and functional;

(4)	The object has proper controls to ensure water temperature does not exceed 210 degrees Fahrenheit;

(5)	The water capacity is less than 120 gallons; and

(6)	The aggregate heat input of the plant is less than 300,000 Btu/hour.

2.	New Installations

A.	Registration and Certification

Before any low pressure boiler is operated in the State of Maine, the owner of the low pressure boiler must register the low pressure boiler with the Board and must obtain a current, valid inspection certificate for the low pressure boiler.

B.	Installation Inspections

(1)	Notification. The owner of a low pressure boiler must notify the State and the owner’s insurance company when applicable before placing a new low pressure boiler in service.

(2)	Inspection. An Inspector must conduct the initial inspection of a low pressure boiler in accordance with the applicable code specified in Chapter 11 of these rules. The initial inspection must consist of an internal and external inspection, if construction permits. The Inspector must report the results of the inspection to the Board on forms provided by the Board.

# C.	Relocation. Before a relocated low pressure boiler is installed, the owner must petition the Chief Inspector for a variance to approve the installation. The Chief Inspector must perform the initial inspection of a relocated boiler.

3.	Existing Low Pressure Boilers

A.	Rules Applicable to Construction and Installation. The design, construction, construction-related inspection, installation, and stamping of all existing low pressure boilers must comply with the rules of the Board in effect at the time of installation.

B.	Rules Applicable after Installation. The maintenance, operation and post-installation inspection of all existing low pressure boilers must comply with the rules of the Board in effect at the time of the maintenance, operation, or post-installation inspection.

4.	Registration Numbers

A.	Display; Not Transferable. The assigned State of Maine registration number must appear on each low pressure boiler at all times. The registration number assigned to a low pressure boiler may not be transferred to another boiler.

B.	Low Pressure Boiler Numbers. The Inspector must place the assigned State of Maine registration number, preceded by the letter “H,” on a self-locking metal tag issued by the Board and must affix the tag to a suitable fitting on the low pressure boiler.

# 5.	Periodic Inspections of Low Pressure Boilers

A.	Inspection Methods and Frequency. Before the initial inspection certificate expires, and annually thereafter, all low pressure boilers in the State must be inspected as follows:

(1)	An Inspector must perform 1 annual certificate inspection, which must be an external inspection conducted while the boiler is in operation; and

(2)	When construction permits, an Inspector must perform an internal inspection every third year.

B.	Report. An Inspector must submit to the Board a report of each inspection performed pursuant to Paragraph A on a form approved by the Board.

6.	MAWP of Existing Low Pressure Boilers Not Constructed to Code

The MAWP on the shell of a low pressure boiler or drum shall be determined by the strength of the weakest course computed from the thickness of the plate, the tensile strength of the plate, the efficiency of the longitudinal joint, the inside diameter of the course, and the factor of safety allowed by paragraph A. The formula for determining MAWP is as follows:

# TStE = MAWP, PSIG

# RFS

# Where:

TS	= 	Ultimate tensile strength of shell plates, PSI

R	= 	Inside radius of the weakest course of the shell or drum, inches.

t	= 	Minimum thickness of shell plates in weakest course, inches.

E	= 	Efficiency of longitudinal joint, as calculated in the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of the Board’s rules.

FS 	= 	Factor of Safety allowed by Paragraph A.

A.	Factor of Safety. The factor of safety must be at least 5.

B.	Tensile Strength. When the tensile strength of steel or wrought-iron shell plates is not known, it must be assumed to be 55,000 PSI for steel and 45,000 PSI for wrought iron.

C.	Strength of Rivets. Calculations concerning riveted joints must be those established by the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of these rules, or as approved by the Board.

# 7.	Pitch Horizontal Firetube Boilers

Horizontal firetube boilers must be pitched toward the blow-off outlet not less than 1 inch for each 10 feet of tube length when set.

# 8.	Manual Dampers

Fully closable manual dampers are prohibited on automatically fired low pressure boilers. The owner must ensure that any such existing dampers are removed.

# AUTHORITY: 	32 MRSA § 15104-A(1)

# REPEALED AND REPLACED:

# January 15, 2005 -	filing 2005-24 repealed old Chapter 13

# filing 2005-25 adopted new Chapter 13