02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

#### Chapter 1:	DEFINITIONS

Summary: This Chapter is promulgated to clarify wording of the law and these Rules.

As used in these Rules, the following terms have the following meanings:

1-1	Affidavit. A form provided by the Board to document an applicant’s licensed practical experience.

1-2	ASME. American Society of Mechanical Engineers.

1-3	Board. State of Maine Oil and Solid Fuel Board.

1-4	CANDIDATE INFORMATION BULLETIN. A document provided by the Board describing the examination process including content areas and study material.

1-5	Cleaning of Oil or Solid Fuel Equipment. The process of: brushing and vacuuming a heating appliance heat exchanger, warm air furnace, boiler (steam or hot water) flue passages and connectors, lubricating motors, and bearings; replacing nozzles, belts, filters, and electrodes; performing combustion efficiency testing; and any other procedure for cleaning and annual maintenance as described in the manufacturer’s instructions.

1-6	COMBINATION UNIT. A combination unit is a heating appliance that is listed for the use of more than one fuel in the same vessel.

1-7	Combustion Efficiency Test. A test conducted to determine efficiency of combustion by measuring the composition and temperature of flue gases as they leave the appliance.

1-8	ENT FLEXIBLE CONDUIT. Electrical Non-Metallic Tubing.

1-9	GPH. Gallons per hour.

1-10	INSTALLATION. The installation, alteration or repair of oil and solid fuel burning equipment, chimneys and fireplaces, including accessory equipment.

1-11	LABELED. The certification of equipment or materials by a label, symbol, or other identifying mark by a nationally recognized testing agency of an organization which conducts periodic inspection of equipment and materials to indicate compliance with appropriate standards of performance.

1-12	License Authority. The scope of permission granted to service and install various types of oil and solid fuel burning equipment to each license category, e.g., 1 and 2 oils over 15 gph, 1 and 2 oils over 15 gph/solid fuel, 1 and 2 oils up to 15 gph, 1 and 2 oils up to 15 gph/solid fuel, 1-6 oils, 1-6 oils/solid fuel, 4-6 oils, 4-6 oils/solid fuel.

1-13	LISTED. The determination that a piece of equipment or material meets appropriate standards for specific purposes established by a nationally recognized testing agency.

1-14	Practical Experience. Actual work performed on oil and solid fuel burning equipment while holding a valid license issued by the Board.

1-15	Rules. Rules adopted by the Oil and Solid Fuel Board.

1-16	SIGNING MASTER. A licensed Master Oil Burner and/or Solid Fuel Technician who signs an Apprentice application or an application for examination acknowledging employment or supervisory responsibility for the work ethics, performance, and training required of the applicant.

1-17	Supervision. The direction and overseeing of the work and performance of a licensed apprentice or journeyman as clarified below:

1-17.1	Direct Supervision: Supervision which is provided to an apprentice by a licensed master or journeyman which requires that the master or journeyman be on site at all times.

1-17.2	Indirect Supervision: Supervision which is provided to a journeyman by a licensed master which does not require the master to be on site at all times.

AUTHORITY: 32 M.R.S.A. §2311, §2353, and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

Chapter 2:	ADVISORY RULINGS

Summary: This rule establishes guidelines relating to advisory rulings.

2-1	ADVISORY RULINGS

2-1.1	Authority and Scope

The Board may issue an advisory ruling in accordance with 5 M.R.S.A. §9001 concerning the applicability of a statute or rule to existing facts. The Board shall review each request for an advisory ruling to determine whether the requested ruling is appropriate. The Board may, at its discretion, decline to issue an advisory ruling if the question is hypothetical, if there is insufficient information upon which to base a ruling or for any other reason the Board deems proper.

2-1.2	Submission

A request for an advisory ruling must be submitted to the Board in writing and must set forth in detail all facts pertinent to the question. The Board may require submission of additional information it deems necessary to provide a complete a factual background.

2-1.3	Ruling

The Board shall issue advisory rulings in writing. The advisory ruling must include a statement of facts or assumptions, or both, upon which the ruling is based. The statement, without reference to other documents, must be sufficiently detailed to apprise the reader of the basis of the opinion. The assent of four members of the Board is required for the issuance of an advisory ruling. The ruling must be signed by the Board’s Chair, must be identified specifically as an advisory ruling and must be numbered serially.

2-1.4	Publication

The Department shall mail the advisory ruling to the requesting party and the Board Administrator shall retain a copy. An advisory ruling is a public document and is available for public inspection during the normal working hours of the Board. In addition, the Board may otherwise publish or circulate an advisory ruling as it deems appropriate.

AUTHORITY: 5 MRSA §§ 8051, 9001(4)

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 3:	CATEGORIES AND RESPONSIBILITIES OF LICENSURE

Summary: This Chapter describes the duties and responsibilities for licensure as an Apprentice, Journeyman and Master Oil Burner and/or Solid Fuel Technician or as a Limited Tank Installer.

## 3-1	APPRENTICE OIL Burner AND/OR SOLID FUEL TECHNICIAN

3-1.1	An apprentice oil burner technician must be under the direct supervision of a journeyman or master oil burner technician at all times while altering, repairing, or installing oil burning equipment. However, an apprentice oil burner technician may clean oil burning equipment without direct supervision if the licensee has either: (1) successfully completed at least 160 hours of training approved by the Board; or (2) completed at least one (1) year of supervised oil burner experience. The apprentice oil burner technician may also bleed an oil burner without direct supervision. If the oil burner fails to operate properly after bleeding, the apprentice shall refer the problem to a journeyman or master licensee. Failure to conform to this requirement may subject the apprentice and the signing master to disciplinary action for servicing oil burning equipment without proper supervision.

3-1.2	Capabilities are limited to the following license authorities:

3-1.2.1	1 & 2 oils up to 15 GPH.

3-1.2.2	1 & 2 oils over 15 GPH.

3-1.2.3	4, 5, & 6 Oils.

3-1.2.4	1-6 Oils.

3.1.2.5.	Solid Fuel.

3-1.3	A solid fuel apprentice technician must be under the direct supervision of a master solid fuel technician at all times while cleaning, altering, repairing, and installing central solid fuel appliances and accessory equipment.

3-1.4	In order for an apprentice oil burner and/or solid fuel technician to progress through the various licensing categories and authorities, documented proof of licensed practical experience must be provided to the Board. It is the responsibility of the licensee to obtain an affidavit from all masters as to the dates (day, month, year) of accumulated licensed practical experience to establish his or her eligibility when applying for a higher category or authority of license.

3-1.5	An apprentice licensee is not permitted to work on any oil and/or solid fuel burning equipment if for any reason he is no longer employed or supervised by an appropriately licensed master.

3-1.6	A master and/or journeyman oil burner technician can clean a combination unit and service and repair the oil burner assembly if he or she is licensed as an apprentice solid fuel technician.

## 3-2	JOURNEYMAN OIL BURNER TECHNICIAN.

3-2.1	In order for a journeyman oil burner technician to progress through the various licensing categories and authorities, documented proof of licensed practical experience must be provided to the Board. It is the responsibility of the licensee to obtain an affidavit from all licensed master oil burner technicians who provided supervision as to the dates (day, month, year) of accumulated licensed practical experience to establish his or her eligibility when applying for a master license.

3-2.2	Capabilities are limited to the following license authorities:

3-2.2.1	1 & 2 oils up to 15 gph.

3-2.2.2	1 & 2 oils over 15 gph.

3-2.2.3	4, 5, & 6 Oils.

3-2.2.4	1-6 Oils.

3-2.3	A journeyman oil burner technician must at all times be under the indirect supervision of, or the employ of, a licensed master oil burner technician who accepts full responsibility for the work ethics and performance of the journeyman.

3-2.4	A journeyman oil burner technician is not permitted to work on any oil burning equipment if for any reason he is no longer employed or supervised by a master.

3-2.5	A journeyman oil burner technician cannot supervise an apprentice oil burner technician whose licensing authority exceeds that of the journeyman.

## 3-3	MASTER OIL BURNER AND/or SOLID FUEL TECHNICIAN

3-3.1	Capabilities for a Master Oil and/or Solid Fuel Technician are limited to the following license authorities:

3-3.1.1	1 & 2 oils up to 15 gph.

3-3.1.2	1 & 2 oils over 15 gph.

3-3.1.3	4, 5, & 6 Oils.

3-3.1.4	1-6 Oils.

3-3.1.5	Solid Fuel.

## 3-3.2	Responsibility of the supervising Master

3-3.2.1	By signing an application as supervising master, the master acknowledges employment or supervisory responsibility for the work ethics, performance, and training required of the applicant regardless of the licensing category. It is the duty of the master to personally inspect any installation work performed by any licensee for whom the master is responsible at the conclusion of the installation.

3-3.2.2	Whenever the supervising master ceases to provide supervision, the supervising master shall notify the Board and licensee in writing, a copy of which shall be kept in both the applicant’s and the supervising master’s file.

3-3.2.3	Upon request, the supervising master must provide a signed affidavit documenting all practical experience performed by an apprentice or journeyman under the master’s supervision.

3-3.2.4	A master cannot supervise an apprentice or journeyman whose licensing authority exceeds that of the master.

3-3.2.5	Licensed masters who sell, contract, dispatch, or subcontract any work or installation to another master or other licensee are responsible for the completion of the installation and the work performed. The master contracting the work and the licensee performing the work both have equal responsibility to ensure that all work complies with the Rules adopted by the Board.

## 3-4	LIMITED TANK INSTALLER

A person licensed as a limited oil tank installer is limited to installing outside residential oil supply tanks connected to manufactured housing units as set forth in 10 M.R.S.A. §9002(7)(A).

## 3-5	LIMITED ENERGY AUDITOR TECHNICIAN

3-5.1	A limited energy auditor technician is limited to performing combustion safety and efficiency testing on oil-fired space heating or water heating equipment. Limited energy auditor technicians may not make any adjustments to oil-fired space heating or water heating equipment.

3-5.2	Prior to performing a combustion safety and efficiency test, a limited energy auditor technician shall obtain the manufacturer’s installation and operating instructions for the specific equipment to be tested.

3-5.3	A limited energy auditor technician shall observe all provisions of the manufacturer’s installation and operating instructions when performing a combustion and efficiency test, including but not limited to any restrictions or limitations relating to equipment access and pipe penetration.

3-5.4	Combustion efficiency test results must fall within the guidelines contained in the manufacturer’s installation and operating instructions. The limited energy auditor technician shall provide a copy of the test results to the homeowner and shall notify the homeowner and occupant in writing if the test results do not meet the manufacturer’s guidelines.

AUTHORITY: 32 M.R.S.A. §2311, §2353, §2401 and §2402-A; PL 2007, c. 392, §3

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 4:	QUALIFICATIONS FOR LICENSURE

Summary: This Chapter sets forth the qualifications for licensure as an apprentice, journeyman and master oil burner and/or solid fuel technician or as a limited tank installer and describes the application and examination process.

## 4-1	APPRENTICE OIL burner TECHNICIAN

4-1.1	Applications for licensure must be made on forms provided by the Board and must be accompanied by the fees established by the Director.

4-1.2	The apprentice license application must be signed by an appropriately licensed Master. By signing the application, the signing master acknowledges employment or supervisory responsibility for the work ethics, performance, and training required of the apprentice.

4-1.3	The signing master’s authority must be equal to or higher than the requested authority of the apprentice license. For example, if the authority of the signing master is 1 & 2 oils up to 15 gallons, the apprentice oil licensee may not perform work beyond that authority. Any licensed master or journeyman may supervise an apprentice, provided the master or journeyman has equal to or higher authority than the apprentice.

4-2	APPRENTICE SOLID FUEL TECHNICIAN

4-2.1	Applications for licensure must be made on forms provided by the Board and must be accompanied by the fees established by the Director.

4-2.2	The apprentice license application must be signed by an appropriately licensed Master. By signing the application, the signing master acknowledges employment or supervisory responsibility for the work ethics, performance, and training required of the apprentice.

4-2.3	The signing master’s authority must include solid fuel.

## 4-3	JOURNEYMAN OIl TECHNICIAN

4-3.1	Education and Experience. Table 4-3 sets forth the different combinations of education and experience which qualify a person to sit for the journeyman examination. Out-of-state applicants must have acquired substantially equivalent experience. Applicants qualifying for examination using Path 1 of Table 4-3 may apply and sit for examination upon successful completion of the requisite education prior to meeting the experience requirement.

4-3.2	In-State applicants shall provide documentation of licensed experience on affidavit forms provided by the Board. The affidavit forms must be completed and signed by an appropriately licensed master attesting to the supervision of the applicant’s practical experience.

4-3.3	Out-of-State applicants shall provide documentation of employment as an oil and/or solid fuel technician. This documentation must include one year of actual work performed on oil burning equipment or solid fuel burning equipment.

TABLE 4-3

EDUCATION AND /OR EXPERIENCE REQUIRED TO SIT FOR JOURNEYMAN EXAMINATION

|  | Examination Type | Education | Prerequisite Apprentice License | Journeyman License Experience Requirements |
| --- | --- | --- | --- | --- |
| Path 1 | Journeyman 1 & 2 Oils up to 15 gph Journeyman 1 & 2 Oils over 15 gph Journeyman 4, 5 and 6 Oils | Successful completion of an oil burner technician course at a Maine community college, applied technology center or applied technology region or a comparable institute in Maine or another state consisting of a minimum of 160 hours of study, at least 75 hours of which are made up of laboratory work on oil burning equipment and related systems. If the oil burner technician course contains classroom and laboratory work in 1 and 2 oils over 15 gph and/or 4, 5 and 6 oils, the student will be eligible to apply for the journeyman examination in those license authorities. | Not required unless performing work beyond the classroom. | Six months as a licensed Apprentice. |
| Path 2 | Journeyman 1 & 2 Oils up to 15 gph Journeyman 1 & 2 Oils over 15 gph Journeyman 4, 5 and 6 Oils | Successful completion of one-year accredited heating course at a Maine technical college consisting, of a minimum of 320 hours of study, at least 150 hours of which are made up of laboratory work on oil burning equipment and related systems. If the oil burner technician course contains classroom and laboratory work in 1 and 2 oils over 15 gph and/or 4, 5 and 6 oils, the student will be eligible to apply for the journeyman examination in those license authorities. | Not required unless performing work beyond the classroom. | No licensed experience required. |

| Path 3 | Journeyman 1 & 2 Oils up to 15 gph Journeyman 1 & 2 Oils over 15 gph Journeyman 4, 5 and 6 Oils | None | Required. | One year of licensed practical experience as an Apprentice doing service and installation work on oil burning equipment. |
| --- | --- | --- | --- | --- |

## 4-4	Master oil burner TECHNICIAN

4-4.1	Qualifications to Sit for Examination. Table 4-4 sets forth the qualifications to sit for the master oil burner technician examination. Out-of-state applicants must have acquired substantially equivalent experience.

4-4.2	In-State applicants shall provide documentation of licensed experience on affidavit forms provided by the Board. The affidavits must be completed and signed by the appropriately licensed master attesting to supervision of the applicant’s practical experience.

4-4.3	Out-of-State applicants shall provide documentation of employment as an oil burner technician. This documentation must include four years of actual work performed on oil burning equipment.

4-5	MASTER SOLID FUEL TECHNICIAN

4-5.1	Qualifications to Sit for Examination. Table 4-4 sets forth the qualifications to sit for the master solid fuel technician examination. Out-of-state applicants must have acquired substantially equivalent experience.

4-5.2	In-State applicants shall provide documentation of licensed experience on affidavit forms provided by the Board. The affidavits must be completed and signed by the appropriately licensed master attesting to supervision of the applicant’s practical experience.

4-5.3	Out-of-State applicants shall provide documentation of employment as a solid fuel technician. This documentation must include two years of actual work performed on solid fuel burning equipment.

### TABLE 4-4

QUALIFICATIONS TO SIT FOR MASTER EXAMINATION

| Examination Type | Prerequisite Journeyman License | Master License Experience Requirements |
| --- | --- | --- |
| Master Oil Burner Technician Master 1 & 2 Oils up to 15 gph Master 1 & 2 Oils over 15 gph Master 4, 5 and 6 Oils | Journeyman license required unless currently licensed as a Master with a different license authority. If currently licensed as Master, the Master may apply for a license as an apprentice in another license authority to gain licensed experience as an apprentice to qualify for an additional license authority. See Chapter 5 of these Rules. | Four years of licensed practical experience, a minimum of two years of which must be as a licensed journeyman, doing service and installation work on oil burning equipment. |
| Master Solid Fuel Technician Master Solid Fuel | Not Required. | Two years of licensed practical experience as an Apprentice with the Solid Fuel authority doing service and installation work on central solid fuel burning equipment. A licensed master oil technician can sit for the master solid fuel examination without acquiring any solid fuel practical experience. |

4-6	LIMITED TANK INSTALLER

4-6.1	In order to qualify for a limited tank installer’s license, an applicant must hold and maintain either a manufactured housing mechanic’s license or a manufactured housing dealer’s license issued pursuant to 10 M.R.S.A. Chapter 951 or be a manufactured housing dealer employee who has satisfactorily completed a training program that includes at least four (4) hours on installation of outside oil tanks, as approved by the Board.

4-6.2	Applications for a limited tank installer’s license as set forth in 32 M.R.S.A. §2401 must be submitted on forms provided by the Board, together with evidence of satisfactory completion of a training program approved by the Board and must be accompanied by the fees established by the Director.

4-6.3	The training program approved by the Board is valid for one (1) year from successful completion. If an applicant fails to apply for a license within one (1) year from completion of a training program approved by the Board, the applicant must retake the training program.

4-6.4	Experience gained as a limited tank installer cannot be used to satisfy the prerequisite needed to obtain a master or journeyman oil technician’s license.

## 4.7	LIMITED ENERGY AUDITOR TECHNICIAN

4-7.1	In order to qualify for a limited energy auditor technician license, an applicant shall provide evidence of satisfactory completion of the Certified Building Analyst 1 certification test and field examination offered by the Building Performance Institute, the equivalent Maine residential energy auditor certification program, or an equivalent training program acceptable to the Board.

4-7.2	Each applicant for a limited energy auditor technician license as set forth in 32 MRSA §2401-B(2-A) shall apply by completing and submitting forms provided by the Board, together with evidence of satisfactory completion of the Certified Building Analyst 1 certification test and field examination offered by the Building Performance Institute, the equivalent Maine residential energy auditor certification program, or an equivalent training program acceptable to the Board.

4-7.3	Experience gained as a limited energy auditor technician may not be used to satisfy the prerequisites for licensure as a master or journeyman oil burner technician.

## 4-8	criteria for examination AND LICENSURE FOR MULTIPLE AUTHORITIES

4-8.1	Criteria for examination and licensure for multiple authorities for journeyman oil burner technician and master oil burner and/or solid fuel technicians shall be as follows:

4-8.1.1	To be eligible for a 1 & 2 over 15 gph license, the applicant must have passed the examination for both the 1 & 2 oil up to 15 gph and the 1 & 2 oils over 15 gph. An applicant seeking both 1 & 2 (light) oils up to 15 gph and the 1 & 2 (light) oils over 15 gph license, may acquire the licensed experience concurrently.

4-8.1.2	To be eligible for a 1-6 oils license, the applicant must have passed the examination for both the 1 & 2 (light) oils up to 15 gph, and 4, 5, & 6 (heavy) oils. An applicant seeking both 1 & 2 (light) oils up to 15 gph and the 4, 5, & 6 (heavy) oils license, may acquire the licensed experience concurrently.

4-8.1.3	The signing master’s authority must be equal to or higher than the requested authority of the applicant. For example, the authority of the signing master is 1 & 2 oils up to 15 gph the applicant may not apply beyond that authority.

## 4-9	Application for Examination

4-9.1	Applicants for examination(s) must submit all of the following:

4-9.1.1	Completed Application;

4-9.1.2	Application Fee (nonrefundable);

4.9.1.3	School Certificate(s) (if applicable); and

4-9.1.4	Affidavit(s)

4-9.2	Incomplete or illegible applications will be returned to the applicant together with any attachments.

4-9.3	Applicants must receive Board approval prior to sitting for an examination. Examination scores of applicants who take an examination prior to receiving Board approval will be null and void.

## 4-10	Examination(s)

4-10.1	The passing score for all examinations is 70%.

4-10.2	The Board will mail a license application to a candidate who successfully passes the examination.

4.10.2.1	An examination application will remain valid for a period of two (2) years from the date of receipt. If an applicant fails to pass the examination within two (2) years of Board approval, the applicant must reapply as a new applicant. If an applicant fails to apply for a license within two (2) years from the date of notification of a passing score on the examination, the applicant must reapply as a new applicant and retake the examination.

NOTE: Refer to the Candidate Informational Bulletin for more examination information.

## 4-11	Renewal of license

4-11.1	Expiration. All licenses expire two (2) years from the date of issuance.

4-11.2	Eligibility for Renewal. To renew a license, an applicant must comply with 32 M.R.S.A. §2404. A license may be renewed up to 90 days after expiration upon payment of a late fee in addition to the renewal fee.

## 4-12	Reinstatement of license

4-12.1	More than 90 Days but not more than 2 Years. Individuals, other than formerly licensed apprentices who fail to renew a license for more than 90 days but not more than two (2) years from the date of expiration may reinstate the license without taking the examination by filing a new application for renewal and by filing and paying the license fee and penalty as set forth in the Office of Licensing and Registration Rules Chapter 10, Establishment of License Fees, Section 5. An apprentice must reapply as a new applicant.

4-12.2	More than Two Years. An individual who fails to renew a license for more than two (2) years from the date of expiration must obtain a new license by satisfying all of the requirements of 32 M.R.S.A. Chapter 33 and these Rules.

AUTHORITY: 32 M.R.S.A. §2353, §2402-A, §2403, and §2404; PL 2007, c. 392, §3

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

Chapter 5:	USE OF OTHER LICENSE AUTHORITIES

Summary: This Chapter sets forth the requirements for licensed master and journeyman technicians to gain licensed experience as an apprentice to qualify for an additional license authority. Current license authorities are: 1&2 Oils Up to 15 gph, 1&2 Oils Over 15 gph, 4, 5 & 6 Oils and Solid Fuel.

5-1	In order for a licensed journeyman or master to be eligible to take an examination in another license authority, the applicant must:

5-1.1	Submit the proper application, appropriate fees, and an affidavit attesting to the requisite supervision for the relevant license as follows:

5-1.1.1	A licensed journeyman applying for a journeyman examination for a different authority must provide documented proof of one (1) year of direct supervision.

5-1.1.2	A licensed journeyman applying for a solid fuel master examination must provide documented proof of two (2) years of direct supervision.

5-1.1.3	A licensed master applying for a master examination of a different authority must provide documented proof of one (1) year of indirect supervision.

5-1.1.4	A licensed master oil burner technician applying for a master solid fuel examination is automatically qualified.

5-1.2	Whenever the supervising master ceases to provide supervision, the supervising master shall notify the Board and licensee in writing, a copy of which shall be kept in both the applicant’s and the supervising master’s file.

5-1.3	An apprentice license issued to a licensed master or journeyman to gain experience towards an additional authority does not expire.

5-1.4	The apprentice license fee will be waived for licensed masters or journeymen gaining licensed experience to qualify for an additional license authority. The applicant will be required to pay an application fee.

AUTHORITY:	32 M.R.S.A. §2353 and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 7:	ADOPTION OF STANDARDS AND RULES

Summary: This Chapter sets forth the standards for installation of any oil and solid fuel burning equipment, chimneys, fireplaces and vents.

7-1	The Oil and Solid Fuel Board adopts and incorporates herein the following editions of technical standards or codes issued by the National Fire Protection Association and Rules promulgated by the Board. All installations of any oil and solid fuel burning equipment, the installation of chimneys, fireplaces and vents shall comply with applicable requirements of these standards and additional standards imposed by Title 32, Chapter 33 and these Rules.

NFPA #30 A, Motor Fuel Dispensing Facilities and Repair Garages 2003 edition

NFPA #31, Standard for the Installation of Oil Burning Equipment 2006 edition (See 7-2 below)

NFPA #211, Chimneys, Fireplaces, Vents, and Solid Fuel Appliances 2006 edition (See 7-2 below)

NFPA #70, National Electrical Code 2005 edition

NFPA #88 A, Parking Structures 2002 edition

NFPA #90 A, Installation of Air Conditioning and Ventilating Systems 2002 edition

NFPA #90 B, Warm Air Heating and Air Conditioning Systems 2006 edition

7-2	Exceptions

7-2.1	NFPA #31, Standard for the Installation of Oil Burning Equipment (2006 edition).

7-2.1.1	The Board does not adopt Chapter 7, Section 7.13.3, Fuel Oil Storage Systems that Are Permanently or Temporarily Taken Out of Service.

7-2.1.2	The Board does not adopt Chapter 8, Section 8.7.10.1, Vent pipe sizing. (See Chapter 9.12.3.7).

7-2.2	NFPA #211, Chimneys, Fireplaces, Vents, and Solid Fuel Appliances (2006 edition) is adopted by the Board with the following exceptions:

7-2.2.1	The Board does not adopt Chapter 11, Fireplaces.

7-2.2.2	The Board does not adopt Chapter 12, Solid Fuel-Burning Appliances, Section 12.5.1.2, Room Heaters, Fireplace Stoves, Room Heater/Fireplace Stove Combinations, and Ranges.

7-2.2.3	The Board does not adopt the following Sections of Chapter 13:

7.2.2.3.1	Section 13.2, Annual Inspection, the reference to the requirements of Section 14.3;

7.2.2.3.2	Section 13.4.1 of Section 13.4, Appliance or Connector Replacement, the reference to Chapter 14; and

7.2.2.3.3	Section 13.7.2 of Section 13.7, Evidence of Damage.

7-2.2.4	The Board does not adopt Chapter 14, Inspection of Existing Chimneys.

7-3	The above NFPA standards and Rules may be purchased from:

7-3.1	NFPA Publications

National Fire Protection Association

1 Batterymarch Park

P.O. Box 9101

Quincy, MA 02269-9101

Telephone: 1-800-344-3555

  - The Oil and Solid Fuel Board incorporates herein the following Appendices:

    - 7-4.1	Appendix A – Department of Environmental Protection Oil Regulations

    - 7-4.2	Appendix B – Department of Environmental Protection Asbestos Regulations

    - 7-4.3	Appendix C – Memorandum of Understanding between the Oil and Solid Fuel Board and the Plumbers’ Examining Board regarding the installation of hot water or steam and warm air heating systems.

    - 7-4.4	Appendix D – Memorandum of Understanding between the Oil and Solid Fuel Board and the Propane and Natural Gas Board for the installation of hot water or steam heating systems.

    - 7-4.5	Appendix E – Memorandum of Understanding between the Oil and Solid Fuel Board and the Electricians’ Examining Board for the Installation, Service and Repair of Hot Water, Steam, Warm Air Heating Systems and Oil Fired Hot Water Heaters.

7-4.6	Appendix F - State of Maine Emergency Chimney Update Waiver Form.

7-4.7	Appendix G - Chimney or Fireplace Construction/ Installation Disclosure.

7-5	The above appendices are included in the back of these Rules or may be obtained from the Oil and Solid Fuel Board.

Authority: 32 M.R.S.A. §2313, §2353, and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

Chapter 8:	MODIFICATION OF STANDARDS

Summary: This Chapter allows the Board to authorize modifications to installation under unusual circumstances. This Chapter provides the Board with the discretion to alter installation standards after appropriate technical consideration.

8-1	Where the circumstances or conditions of any particular installation are unusual as to render the strict application of a standard imposed by Board Rules and regulations impractical, the Board, or its designees (Compliance Officers located at the Department of Professional and Financial Regulation), may permit such modifications as will provide a substantially equivalent degree of safety and be consistent with good engineering practice.

8-2	Application for permission to deviate from installation standards imposed by the Board Rules shall be made in writing and shall document why compliance with a prescribed standard is technically impractical and how the proposed modification would meet the equivalent degree of safety. The Board may request any additional information it deems necessary to assure that the modification provides a reasonable degree of safety.

8-3	The Board may grant authority to deviate from a particular Rule(s). Such decision shall be in writing, and shall convey authority to adopt modifications only for the specific installation described in the application and no other.

Authority: 32 M.R.S.A. §2313, §2353 and §2402

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 9:	INSTALLATION OF OIL BURNING EQUIPMENT

Summary: This Chapter sets forth the guidelines for the installation of oil burning equipment with necessary safety controls, devices and standards for the reduction of fire hazards associated with oil fired equipment used in residential, commercial, and industrial applications.

## 9-1	NATIONALLY ACCREDITED TESTING LABORATORY

All heating, chimney and/or fireplace equipment installed as well as any accessory equipment installed must be listed as approved by Underwriters’ Laboratories or by a nationally accredited testing laboratory, with certification that applicable national and Maine standards have been met. Such listing must be in effect at the time of installation.

## 9-2	WORKMANSHIP

All work shall be conducted, installed, and completed in a professional manner.

## 9-3	UNLAWFUL ACTS

It shall be unlawful for any person, firm, or corporation to erect, construct, alter, repair, or install oil burning equipment regulated by these Rules and standards, or cause same to be done, in conflict with or in violation of any of the provisions of these Rules.

## 9-4	SERVICE AND REPAIR OF EQUIPMENT

Service and repair of any system or replacement of parts shall be permitted to be made in the same manner as it was in the existing system provided that such repair or replacement is not hazardous and that all material, equipment and devices shall be constructed and installed in accordance with their specific purpose and listing and comply with current Rules.

## 9-5	MAINTENANCE

9-5.1	All oil burning equipment and systems, both new and existing, and parts thereof shall be maintained in a safe condition.

9-5.2	When performing any service on a customer’s heating system, the licensee must notify the homeowner of any code violations and make recommendations to address them.

9-5.3	When performing an annual tune-up on a heating system, a combustion efficiency test must be conducted and a copy of the test must be posted on-site.

## 9-6	INSTALLATIONS

9-6.1	Whenever a furnace, direct-fired hot water heater, or boiler is installed, the total installation must be brought into compliance with the requirements of NFPA # 31 and all other Rules adopted by the Board BEFORE the furnace, direct-fired hot water heater, or boiler is fired. Prior to leaving the installation (whether installed inside or outside any structure) unsupervised, the licensed oil burner and/or solid fuel technician shall observe, inspect, and test the equipment to ensure that the installation is operating safely and properly and meets all applicable Rules.

9-6.2	Whenever a new burner is installed, the wiring shall be brought into compliance with the requirements of these Rules before the unit is fired. The wiring update must include the following:

9-6.2.1	Properly rated fuse or breaker.

9-6.2.2	Properly rated wiring.

9-6.2.3	Properly installed and located emergency switch.

9-6.2.4	Properly installed and located thermal electric switch.

9-6.2.5	Properly installed and located service switch.

9-6.2.6	Properly installed and located low water cut-off.

9-6.3	When performing an installation, a combustion efficiency test shall be conducted and a copy of the test results shall be posted on-site.

9-6.4	When an emergency situation arises that does not allow adequate time to get the chimney lined and/or repaired before installing the new heating appliance, the licensee may defer the required repairs for up to 90 days. It is the licensee’s responsibility to ensure that the installation meets all standards adopted by the Board and the manufacturer’s instructions. The licensee must either install or have installed the required liner or make the proper repairs within the 90 day time period. An emergency situation may include, but is not limited to, situations of serious equipment failure, such as a cracked heat exchanger of a warm air furnace or a leaking boiler in cold weather. Emergency situations may also include failure of equipment that generates hot water and the unavailability of a chimney professional. (See Appendix F)

9-6.5	Heat Loss Requirement

9-6.5.1	New Installations. Heat loss system design and system load calculations for all new installations shall be performed prior to the installation. The licensee must retain a copy of the heat loss system design and system load calculations such that it may be produced for inspection upon request of the board compliance officers.

9-6.5.2	Replacement Systems. A heat loss and/or load calculation shall be conducted before replacement. The licensee must retain a copy of the heat loss system design or system load calculations, or the stamped plans of an engineered system, such that they may be produced for inspection upon request of the board compliance officers.

## 9-7	Low Water Control for OIL FIRED Boilers

9-7.1	All oil-fired boilers shall be provided with a properly installed and operating low-water control.

9-7.2	The low-water control may be installed in, or attached to, the boiler at the level recommended by the boiler manufacturer, but in no case shall the low-water control be installed below the crown sheet. The low-water control, when not installed directly in the boiler, may be installed either in the main supply line (Vertical riser) as close to the boiler as possible, or in a water column of continuous piping attached directly to the boiler.

9-7.3	The low-water cut off shall be designed and approved for the medium used (steam or water).

9-7.4	No valves or other obstructive devices shall be installed between the boiler and safety controls or devices.

## 9-8	Piping, Pumps and Valves

9-8.1	Supply Connections/Oil Shut-off Valves

9-8.1.1	A listed lever or wheel, thermally-operated oil shut-off valve designed to shut off the oil supply in case of fire, shall be installed at the burner and at the oil supply tank.

9-8.1.1.1	When outside tanks are used, a thermally operated shut-off valve shall be installed where the supply line enters (inside) the building.

9-8.1.1.2	When inside tanks are used and the oil supply tank is installed in a separate room, a thermally operated shut-off valve shall be installed where the line enters the room where the appliance is located.

9-8.1.2	Whenever the oil supply is taken from the top of an oil tank, whether the oil tanks are outside or inside, a thermally operated wheel or lever type shut-off valve shall be installed at the tank and at the burner for control of the fuel. A check valve may be used in the supply line, but no valve or obstruction shall be placed in a return line connected to a burner or pump.

9-8.2	Thermally-Operated Valves. Thermally operated valves over ½ inch that are not currently listed may be installed upon receipt of written approval of a Board Inspector. The written approval must be requested and received prior to installation.

## 9-9	Oil Supply and Return Piping

9-9.1	Whenever a copper oil supply or return line is installed under cement, sub-floors, or earth surface, it shall be continuous from the burner to the tank without any splices.

9-9.2	In order to avoid undetected oil leaks under floors, all copper oil supply and return lines installed under cement, sub floors, or beneath any surface, shall be encased in a continuous piece of non-metallic, liquid tight conduit such as PVC, ENT, or other approved material. The conduit shall be a minimum of one (1) pipe size larger than the oil supply and return lines. The ends of the conduit shall penetrate the cement or earth surface a minimum of two (2) inches above grade. All copper tubing, spliced within an oil supply line, shall be made above the surface of the cement, sub-floor or earth surface.

9-9.3	Coated copper tubing must have an OSV valve or PRV valve installed at the tank when used underground.

9-9.4	All copper fuel oil lines shall be encased in a continuous piece of non-metallic liquid tight conduit such as PVC, ENT, coated copper tubing, or other approved material and secured in order to prevent physical damage. The end of the conduit shall not exceed more than two (2) inches from any fitting, except the connection at the fuel tank and at the fuel pump located at the burner shall not exceed six (6) inches.

9-9.5	No oil supply line may be concealed in a wall, ceiling, or partition unless access to the oil supply or return line can be had without cutting through existing walls, ceilings or partitions. This may be accomplished by providing removable panels.

9-9.6	Oil supply lines, which penetrate a foundation wall, shall be encased in a non-metallic, liquid tight conduit such as PVC, ENT, or other approved material. The sleeve shall be sealed at the wall to prevent the entry of water, insects, or rodents.

9-9.7	When an oil filter or other accessory equipment is connected to copper piping smaller than three-quarter (3/4) inch, and is not located within the vicinity of the oil supply or burner connections, the filter or other devices shall be rigidly supported by a wall or floor mounted bracket or other means providing sufficient support for stability and servicing this type of accessory equipment.

9-9.8	All oil supply and return lines of copper tubing shall be connected by flare fittings only. All fittings shall be accessible for service or replacement. No compression fittings shall be used on a supply or return oil line unless it is for the introduction of the lines at the top of the tank with a single or double tap bushing.

9-9.9	All connections of supply or return oil lines located outside shall be made with flare frost fittings.

9-9.10	No oil lines or oil devices which are disconnected from an oil supply tank, burner or unit, shall be left open. Any oil line or oil device which is disconnected or discontinued shall be sealed or closed with a plug, cap or other approved fitting.

9-9.11	Unprotected supply lines that are buried and grouted must be removed from service.

9-9.12	If underground or under-slab piping is connected to a tank of over 660 gallons capacity or to tanks with an aggregate capacity of over 1320 gallons, the installation of the underground piping must meet Department of Environmental Protection requirements. (See Appendix A)

9-9.13	Oil spills must be reported to the Department of Environmental Protection in accordance with Appendix A.

## 9-10	Oil Supply Tanks

9-10.1	Inside Tank Fabrication

9-10.1.1	Rectangular built-in place tanks shall be fabricated using one-quarter (1/4) inch minimum thick steel sheets reinforced on maximum twenty-four (24) inch centers. Tank bottoms shall be supported on twelve (12) inch wide non-combustible piers, to a height of eight (8) inches above the floor. All welding shall be performed by a welder. Tanks shall be designed by a registered engineer who shall observe the tank under 5 PSI test and certify to it being tight under this test.

9-10.2	Manholes

9-10.2.1	Manholes, sixteen (16) inches in diameter or larger, shall be installed in the top of all tanks of 5,000 gallons or more.

9-10.2.2	Manholes provided in 5,000 gallons supply tanks shall be liquid tight when installed inside of a structure.

9-10.2.3	Manholes, when required for outside use, may take the form of a floating lifter roof or weak roof-to-shell seam, or other approved pressure relieving construction.

9-10.3	Clearances. All fuel oil supply tanks must be a minimum of five (5) feet from any gas and/or solid fuel burning appliance.

## 9-11	Outside Oil Supply Tanks

9-11.1	Oil supply tanks shall not be installed on wood or other combustible surfaces or supports.

9-11.2	Outside oil supply tanks of 350 gallons or less shall be supported in accordance with 9-11.3 and 9-11.4.

9-11.3	A horizontal oil supply tank shall be mounted on steel pipe legs, not exceeding twelve (12) inches in height with floor flanges at the base of the steel legs and be supported by four (4), 4 x 8 x 16 inch reinforced concrete blocks, or a one (1) piece reinforced concrete pad not smaller than the tank dimensions. The four (4) blocks or the pad shall rest on a firm subgrade consisting of a bed of compacted, well draining gravel (6 inch minimum), crushed stone (6 inch minimum), or some other subgrade approved by the Board. See Figure 12(a). There must be a minimum of 4” of clearance under the tank from any surface. See Figure 12(a)).

9-11.4	An upright or vertical tank shall be mounted on steel pipe legs not exceeding twelve (12) inches in height, with floor flanges at the base of the steel leg, and supported by a reinforced concrete pad at least three (3) inches thick. The pad's width and length shall not be smaller than the tank dimensions. The pad shall be of one (1) piece construction. The pad shall rest on a bed of compacted, well draining gravel (6 inches minimum), crushed stone (6 inches minimum), or some other subgrade approved by the Board. There must be a minimum of 4 inches of clearance under the tank from any surface. See Figure 12(b).

9-11.5	When installing a vertical fuel oil tank in a listed secondary containment system, the four (4) inch clearance requirement from the bottom of the tank to any surface may be reduced to a minimum of one (1) inch.

9-11.6	The leg brackets welded on the tank shall not be considered a leg and may not be used to rest on the side of the reinforced concrete pad or reinforced concrete blocks.

9-11.7	When a reinforced concrete pad is fabricated on-site, the legs of the supply tanks shall not be embedded as part of the pad.

9-11.8	In all installations, the pipe flanges must be in direct contact with a reinforced concrete pad or reinforced concrete blocks.

9-11.9	Tanks must be disposed of in accordance with the Department of Environmental Protections Rules. Used, underground, oil storage tanks are prohibited from use for aboveground supply of oil except where a Maine registered engineer certifies that the tank meets the requirements of UL 142 and NFPA 30.

9-11.10	Outside tanks and piping must be located such that they are not subject to falling snow or ice. To meet this requirement, the tank and outdoor piping must be installed with a protective cover over the tank valve, oil filter, and any piping which is either without structural support or not attached to the side of the building.

9-11.11	All outside supply tanks shall be held to the same standards as newly installed tanks.

9-11.12	For a single-tank installation, the fuel supply line cannot extend more than twelve (12) inches beyond the face of the tank.

## 9-12	Inside Oil Supply Tanks.

9-12.1	No oil supply tanks may be installed on wood or other combustible surfaces.

9-12.2	The installation of an unenclosed supply tank(s) located inside a building(s) without a finished cement floor, shall be supported by (4) four 4x8x16 inch reinforced concrete blocks or a reinforced concrete pad. The pad shall be at least three (3) inches thick, the width and length extending the full dimensions of the tank. The tank legs shall not exceed twelve (12) inches in height with floor flanges at the base of the steel legs. There must be a minimum of 4 inches of clearance under the tank from any surface.

9-12.2.1	An inside oil supply tank shall be mounted on steel pipe legs not exceeding twelve (12) inches in height. The steel pipe legs or flanges must be in direct contact with a reinforced concrete pad or a reinforced concrete block under each leg.

9-12.2.2	The top of all of the fuel oil tanks on a multiple tank installation shall be on the same horizontal plane.

9-12.2.3	Oil shut-off valves shall be provided immediately adjacent to the burner supply connections at the bottom of the supply tanks.

9-12.2.4	The manifold at the cross connections of the burner supply line, shall be of steel, wrought-iron pipe or copper tubing. (Standards for Steel and Wrought-Iron Pipe, ANSI B36.10). The manifold piping shall be as close to the shutoff valves as possible so that the distance between the tank and the last fitting shall not extend beyond (6) six inches from the face of the tanks and the final fitting (elbow or tee). See Figure 13(b).

9-12.2.5	On multiple tank installations, it is the installer’s responsibility to ensure that return line product will not cause spillage.

9-12.2.6	When installing multiple fuel oil tanks with separate fill pipes and a common venting system, the requirement for increasing the vent pipe one pipe size larger than the largest individual vent pipe shall not be required.

9-12.3	When installing two tanks that are cross connected according to Figure 7.7.1 of NFPA #31, 2006 edition, the gauge must be installed only in the vented tank and all burner supply piping from the tank outlet to the filter installed at the tank must be black iron pipe. The piping connected from the second tank may be either black iron pipe or copper tubing. If the filter is not located at the tank manifold, then copper tubing may be used to connect the black iron pipe manifold to the inlet of the filter.

9-12.4	When removing, replacing, or taking a tank out of service for any period of time, the oil tank fill and vent piping shall be removed from the side of the building.

## 9-13	Vent Alarms

9-13.1	All No. 1 and No. 2 fuel oil tanks from 11 to 5,000 gallon capacity located inside a structure shall have a vent alarm.

9-13.2	All No. 1 and No. 2 fuel oil tanks from 65 to 5,000 gallon capacity located outside shall have a vent alarm.

9-13.3	All vent alarms must be installed according to Manufacturer’s Instructions.

## 9-14	Tank Patches

All oil supply tanks must be liquid tight. Leaking tanks may be temporarily repaired with a tank patch. Any tank so repaired must be replaced within 90 days of the repair.

## 9-15	Used Underground Oil Tanks

Abandoned underground oil storage tanks are prohibited from use for above ground storage of oil, except if approved by the Maine State Fire Marshal or if a Maine professional registered engineer or other person meeting the requirements of Statutes and Rules governing professional engineers practicing in Maine, certifies that the tank meets all applicable specifications and requirements of UL 142 and NFPA #30.

## 9-16	State Internal Plumbing Rules

All piping and safety controls on domestic water heaters and domestic water connections to boilers and heaters shall be made in accordance with the State of Maine Internal Plumbing Code.

## 9-17	Electrical Equipment, Required Control Switches

9-17.1	Thermal Electric Switches. A thermal cut-off switch shall be wired into the burner circuit to shut off the burner in the event of a fire at the unit. The switch shall be placed at the highest point directly above the unit to be fired with the thermal element pointed downwards and shall be placed on the bottom of the floor joist or stringer at the front of the unit. In no case shall it be lower than the point where the flue connector enters the chimney. The switch shall be wired to shut-off the burner, circulating fan, forced or induced draft fan and any remote oil pump that is not an integral part of the burner. A thermal electric switch is required for each oil-fired unit in a multi-appliance installation.

9-17.1.1	On multi-unit installations the emergency and thermal electrical switches shall be wired in series through individual unit relays so that, if one switch is opened, all equipment will be rendered inoperable whenever the "EMERGENCY" switch is opened.

9-17.2	Service Switch

9-17.2.1	A service disconnect switch for control of the burner while observing the flame shall be placed at the unit, within arm’s reach of the technician.

9-17.3	Emergency Switch(es)

9-17.3.1	If the entrance to the boiler room is only accessible from the outside, the emergency switch may be placed at the inside not more than one foot beyond the door opening.

9-17.3.2	An emergency switch shall not be placed outside of any building. If conditions are encountered preventing strict adherence to this standard, a Modification of Standards must be requested from the Board. (See Chapter 8, Modification of Standards)

9-17.3.3	Safety and limiting controls shall not be used to manually start and stop the burner by manual manipulation of the controls, except when permitted by the control manufacturer’s installation and operation instructions for testing.

9-17.3.4	On commercial and industrial equipment, the emergency switch shall be installed in accordance with Figure 23(c) on multi-unit installations. The requirements of 9-17.1.1 shall not apply to one or two-story residences.

9-17.3.4.1	On multi-unit installations, the emergency shut-off switch shall be placed at the outside entrance of the room containing the appliances. The emergency switches and the thermal cut-off switches shall be wired in series through individual unit relays so that, if the emergency switch is opened, all heating equipment in the room and the remote pump set will be rendered inoperable. This application shall also apply if there are two or more appliance rooms in the same building connected to a common fuel supply system.

NOTE:	For Primary Safety Controls, Required Programming and Timings for Burners, refer to ASME CSD-1.

9-17.4	Controls Containing Mercury

9-17.4.1	Thermostats containing mercury must be disposed of according to all Federal and State Regulations. (Refer to Title 38, Section 1663 and check with your local supplier)

## 9-18	Steam Boilers

9-18.1	Steam boilers must be installed according to Manufacturer’s Instructions.

## 9-19	Safety and Pressure Relief Valves

Steam and hot water boilers shall be equipped with listed or approved steam safety or pressure relief valves of appropriate discharge capacity and conforming with ASME requirements (ASME Boiler & Pressure Vessel Code, Section IV, Heating Boilers). A shut-off valve shall not be placed between the relief valve and the boiler or on discharge pipes between such valves and the atmosphere.

## 9-20	Water and Steam Boiler Pipe Supports

9-20.1	Piping shall be supported with pipe hooks, metal pipe straps, bands, brackets, or hangers suitable for the size of the piping and shall be of adequate strength and quality and located at intervals so as to prevent or damp out excessive vibration.

9-20.2	Spacing of supports shall not be greater than shown in Table 9-20.

9-20.3	Supports, hangers, and anchors shall be installed so as to not interfere with the free expansion and contraction of the piping between anchors. All parts of the supporting equipment shall be designed and installed so that they will not be disengaged by movement of the supporting piping.

Table 9-20

Support of Piping

| Steel Pipe, Nominal Size of Pipe (Inches) | Spacing of Supports (Feet) | Nominal Size of Tubing (Inch O.D.) | Spacing of Supports (Feet) |
| --- | --- | --- | --- |
| 1/2 3/4 or 1 1 1/4 or larger (horizontal) 1 1/4 or larger (vertical) | 6 8 10 every floor level | 1/2 5/8 or 3/4 7/8 or 1 | 4 6 8 |

9-21	TEMPORARY Repair of Heat Exchangers

9-21.1	Furnace cement or other materials used to seal cracks in the heat exchanger or parts which provide closure therein may be sealed for a maximum of 45 days with furnace cement or other materials.

9-21.2	Whenever a Compliance Officer conducts an inspection and finds a heat exchanger which has been repaired with furnace cement more than 45 days prior to the inspection, he or she shall order it removed unless a purchase order is provided evidencing that replacement of the heat exchanger is in process.

9-22	Welding of Heat Exchangers

9-22.1	The manufacturer shall be consulted to determine whether the welding of a heat exchanger is feasible and would be consistent with sound engineering practice. The manufacturer shall provide a written statement as to the feasibility of its heat exchanger being welded.

9-22.2	The repair of a heat exchanger by welding shall be performed by a welder in a procedure suitable for the material. It is the responsibility of the master licensee to oversee such repairs.

9-22.3	The master licensee shall receive guidance from the welder as to the feasibility and acceptability, of performing the welding procedure of the metals prior to the repair of any heat exchanger.

9-22.4	After completion of said repairs or welding, the master licensee shall obtain a written statement from the welder documenting that the heat exchanger has been welded, tested, and is acceptable for use without leakage of after-products into the living space.

9-22.5	Written documentation of said repairs or welding shall be provided to the homeowner. The original documentation shall be kept on file by the master licensee who requested the welding. A copy of all the repair documents containing, at a minimum, the following information shall be sent to the Board:

9-22.5.1	The name of the owner and location where the repair was completed;

9-22.5.2	The name and address of the welder;

9-22.5.3	The specific area(s) or location(s) where the repair or welding was performed;

9-22.5.4	Written approval of the repair from the manufacturer;

9-22.5.5	Equipment identification information, i.e. model name, model number, serial number and gross Btu. rating; and

9-22.5.6	The name, address, and license number of the master licensee who requested the repair.

9-22.6	The welding repair of a heat exchanger may be performed once by a State Certified Welder welder. If for any reason the welding repairs have to be done a second time, the master licensee shall notify the Board for approval before attempting to weld a second time. When circumstances are such that the heat exchanger is no longer in production, the master licensee shall request approval from the Board in writing prior to any repairs being performed.

Authority: 32 M.R.S.A. §2313, §2353, and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 10:	INSTALLATION OF SOLID FUEL BURNING EQUIPMENT

Summary: The purpose of this chapter is to specify the proper installation of solid fuel burning equipment in accordance with NFPA #211 (See Chapter 7). These standards and Rules apply to residential, commercial, and industrial installations which are connected to a central heating system.

10-1	NATIONALLY ACCREDITED TESTING LABORATORY

All heating, chimney and/or fireplace equipment, as well as any accessory equipment, installed must be listed and approved by Underwriters’ Laboratories or by a nationally accredited testing laboratory, with certification that applicable national and Maine standards have been met. Such listing must be in effect at time of installation. All equipment must be continually listed by a nationally accredited testing laboratory.

10-2	WORKMANSHIP

All work shall be conducted, installed, and completed in a professional manner.

10-3	UNLAWFUL ACTS

It shall be unlawful for any person, firm, or corporation to erect, construct, alter, repair, or install solid fuel burning equipment regulated by the Board, or cause same to be done, in conflict with, or in violation of, any of these Rules.

10-4	REPAIR OR REPLACEMENT

Repair of any system or replacement of parts, shall be permitted to be made in the same manner as it was in the existing system, provided that such repair or replacement is not hazardous. All material, equipment and devices shall be constructed and installed in accordance with their specific purpose and listing.

10-5	MAINTENANCE

All new or existing solid fuel burning equipment systems and parts shall be maintained in a safe condition. All devices or safeguards, which are required by these Rules, shall be maintained in good working condition.

10-6	APPLIANCES

10-6.1	Solid fuel burning appliances shall be listed and installed in accordance with the terms of their listing.

10-6.2	The manufacturer’s instructions shall be left with the owner.

10-6.3	The installation shall be made by licensed technicians experienced in making such installations.

10-6.4	The installation shall be such as to provide reasonable accessibility for cleaning heating surfaces; removing burners (multi-fuel and/or combination units); replacing motors, controls, air filters, draft regulators, chimney connectors, and other working parts; and adjusting, cleaning, and lubricating parts requiring such attention. This requirement also pertains to the use of stoker fired units.

10-6.5	No combustible material shall be placed adjacent to the solid fuel burning appliance with less clearance than that which is required by the manufacturer, NFPA #211, and these Rules.

10-6.6	Solid fuel burning units shall not be installed where gasoline or any other flammable vapors or gases are likely to be present.

10-6.7	Whenever a solid fuel appliance is installed in conjunction with an oil burning appliance, the oil appliance shall meet the requirements of these Rules and NFPA #31.

10-7	SOLID FUEL IN GARAGES

Solid fuel appliances cannot be installed in any structure which is directly accessible from a garage, whether a major repair, minor repair, or parking garage. Solid fuel fired central heating appliances may be installed in structures which are attached to the garage but which are not directly accessible from the garage. For a major repair garage, the fire wall separation must be two (2) hours. For minor repair and parking garages, the fire wall separation must be one (1) hour. All combustion air must be taken from outside the building. Refer to NFPA 30A for further information.

10-8	Power Failure By-Pass and Valves

10-8.1	A boiler shall be provided with a power failure by-pass and valve in a closed system.

10-8.2	To prevent overheating conditions during a power failure, a normally open zone valve shall be connected to the largest heating loop in the system. A manual by-pass valve shall be installed in case of the failure of the zone valve. This shall be accomplished by installing the zone valve prior to the flow valve and connecting it to the largest loop in the system. The hand valve shall be installed in a loop around the zone valve. See Figure 7(a).

10-8.3	This provision does not apply to listed outdoor solid fuel burning central heating appliances.

10-9	Air Combustion and Ventilation

Solid fuel-burning appliances shall be installed in a location and manner to provide adequate ventilation and combustion air supply to permit proper fuel combustion chimney draft, and maintenance of safe temperatures. Where buildings are so tight that normal infiltration does not provide the necessary air, outside air shall be introduced. (Refer to manufacturer’s instructions).

10-10	Electrical Wiring and Equipment

10-10.1	Electrical wiring and equipment used in connection with solid fuel-burning equipment shall be installed in accordance with NFPA # 70 (National Electrical Code).

10-10.2	Safety control circuits shall be two-wire, one side grounded, having a nominal voltage not exceeding 150 Volts. A safety control or protective device shall be connected so as to interrupt the ungrounded conductor.

10-10.3	The control circuit shall be connected to a power supply branch circuit fused at not more than the value appropriate for the rating of any control or device included in the circuit.

10-11	Boilers and Water Tanks

10-11.1	All piping and safety controls on domestic water heaters and domestic water connections to boilers and heaters shall comply with applicable provisions of the State of Maine Internal Plumbing Code.

10-11.2	All water tanks furnished with boilers shall be supplied with a drain on the bottom of the water tank as per ASME, Sec. 8, Division 1 (Pressure Vessel UG 25 E).

10-11.3	All boilers and pressure vessels shall either have National Pipe Thread connections or be equipped with flanges and adapters that have National Pipe Thread.

10-11.4	Low water protection shall be accomplished in one of the two ways:

10-11.4.1	If the operation of an electric circuit will arrest the combustion process, then a low water cut-off will be satisfactory.

10-11.4.2	If the condition of 10-11.4.1 does not apply, install according to manufacturer’s instructions.

10-12	Safety and Pressure Relief Valves

Steam and hot water boilers shall be equipped with listed or approved steam safety or pressure relief valves of appropriate discharge capacity and conforming with ASME requirements. A shut-off valve shall not be placed between the relief valve and the boiler or on discharge pipes between such valves and the atmosphere.

10-13	Water and Steam Boiler Pipe Supports.

10-13.1	Piping shall be supported with pipe hooks, metal pipe straps, bands, brackets, or hangers suitable for the size of the piping, and shall be of adequate strength and quality, and located at appropriate intervals so as to prevent or damp out excessive vibration.

10-13.2	Spacing of supports shall not be greater than shown in Table 10-13.

10-13.3	Supports, hangers, and anchors shall be installed so as to not interfere with the free expansion and contraction of the piping between anchors. All parts of the supporting equipment shall be designed and installed so that they will not disengage by movement of the supporting piping.

Table 10-13

Support of Piping

| Steel Pipe, Nominal Size of Pipe (Inches) | Spacing of Supports (Feet) | Nominal Size of Tubing (Inch O.D.) | Spacing of Supports (Feet) |
| --- | --- | --- | --- |
| 1/2 3/4 or 1 1 1/4 or larger (horizontal) 1 1/4 or larger (vertical) | 6 8 10 every floor level | 1/2 5/8 or 3/4 7/8 or 1 | 4 6 8 |

10-14	Hand Fired Warm Air Units

When a hand fired solid fuel burning furnace is equipped with a fan to circulate the air, the fan shall be equipped with a fan control.

10-15	Thermostatically-Controlled, Hand-Fired warm air Units

10-15.1	A fail safe 250 degree fahrenheit limit control shall be installed in the supply plenum, not more than ten (10) inches above the top surface of the heat exchanger, and shall extend at least twelve (12) inches into the supply plenum.

10-15.2	The fail safe limit control shall automatically prevent operation of the furnace in the event of power failure, or shut off, or when 250 degrees fahrenheit temperature is reached whether or not the electrical power source is available.

10-15.3	A barometric draft control shall be installed which will operate by draft intensity and be permanently adjusted to limit the draft to a maximum intensity of minus 0.13 inches of water gauge.

10-16	Combination and Multi-Fueled Units.

10-16.1	Units fueled by oil in combination with wood and/or coal or by oil units with wood and/or coal add-ons shall be designed and constructed so that the oil burner and its components shall not be damaged from the solid fuel burning operations.

10-16.2	The installation of a dual or multi-fuel unit shall comply with all applicable standards for the specific fuel being burned whether oil, gas, or solid fuel.

10-16.3	Whenever an oil burner is installed on a multi-fuel unit that is mounted on hinges to provide the use of the same chamber for solid fuel burning, the burner shall be provided with an automatically-operated device, which will shut off the power circuit to the oil burner when the combustion area is opened and the power burner is not in an operating mode.

10-17	TEMPORARY Repair of Heat Exchangers

10-17.1	Furnace cement or other materials used to seal cracks in the heat exchanger or parts which provide closure therein may be sealed for a maximum of 45 days with furnace cement or other materials.

10-17.2	Whenever a Compliance Officer conducts an inspection and finds a heat exchanger which has been repaired with furnace cement more than 45 days prior to the inspection, he or she shall order it removed unless a purchase order is provided evidencing that replacement of the heat exchanger is in process.

10-18	Welding of Heat Exchangers

10-18.1	The manufacturer shall be consulted to determine whether the welding of a heat exchanger is sound engineering practice. The manufacturer shall provide a written statement as to the feasibility of its heat exchanger being welded.

10-18.2	The repair of a heat exchanger by welding shall be performed by a welder in a procedure suitable for the material. It is the burden of a master licensee to oversee such repairs.

10-18.3	The master licensee shall receive guidance from the welder as to the feasibility and acceptability of performing the welding procedure of the metals prior to the repair of any heat exchanger.

10-18.4	After completion of said repairs or welding, the master licensee shall obtain a written statement from the welder documenting that the heat exchanger has been welded, tested and is acceptable for use without leakage of after-products into the living space.

10-18.5	Written documentation of said repairs or welding shall be provided to the homeowner. The original documentation shall be kept on file by the master licensee who requested the welding. A copy of all the repair documents containing, at a minimum, the following information shall be sent to the Board:

10-18.5.1	The name of the owner and location where the repairs was completed;

10-18.5.2	The name, and address of the welder;

10-18.5.3	Specific area(s) or location(s) where the repair(s) or welding was performed;

10-18.5.4	Written approval of the repair from the manufacturer;

10-18.5.5	Equipment identification information, i.e., name, model number, serial number and gross Btu. rating; and

10-18.5.6	The name, address, and license number of the master licensee who requested the repair.

10-18.6	The welding repair of a heat exchanger may be performed once by a welder. If for any reason the welding repairs have to be done a second time, the master licensee shall notify the Board for approval before attempting to weld a second time. When circumstances are such that the heat exchanger is no longer in production, the master licensee shall request approval from the Board in writing for approval prior to any repairs being performed.

10-19	Installation of Combination Units (Solid Fuel/Oil/Gas)

10-19.1	All units fueled by oil or gas in conjunction with solid fuel shall comply with the applicable provisions of NFPA #31 and NFPA #211 (see Chapter 7) and these Rules.

Authority: 32 M.R.S.A. §2313, §2353 and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 11:	CHIMNEYS

Summary: The primary purpose of this Chapter to set forth the rules governing the removal of waste gases, the reduction of fire hazards associated with the construction and installation of chimneys, fireplaces, and venting systems for residential, commercial, and industrial appliances in accordance with NFPA #211 (see Chapter 7) and these Rules.

11-1	NATIONALLY-ACCREDITED TESTING LABORATORY

All heating, chimney and/or fireplace equipment installed, as well as any accessory equipment installed, must be listed and approved by Underwriters’ Laboratories or by a nationally-accredited testing laboratory, with certification that applicable national and Maine standards have been met. Such listing must be in effect at time of installation. All equipment must be continually listed by a nationally-accredited testing laboratory. See Appendix D.

11-2	CHIMNEY DISCLOSURE

Construction of masonry chimney systems require a State of Maine Chimney Disclosure Form to be completed by the installer. (See Appendix G)

11-3	USE OF EXISTING CHIMNEYS

The required two (2) inch minimum clearance to combustible material for interior chimneys and the one (1) inch clearance to combustible material for exterior chimneys is not required when replacing oil fired appliances.

NOTE: The above clearances are required when a solid fuel appliance or a wood stove is connected to the chimney flue.

11-4	Interconnection

11-4.1	Gas utilization appliances and appliances burning liquid fuels may be connected to one chimney flue through separate openings or may be connected through a single opening if joined by a suitable fitting located as close as practical to the chimney provided. (Refer to NFPA #211, see Chapter 7)

11-4.2	The interconnection of oil and solid fuel-burning equipment is not acceptable unless the equipment is specifically listed for such connections.

11-5	USE OF PRIORITY CONTROLS FOR MULTIPLE UNITS.

11-5.1	A priority control for installation of an oil-fired warm air furnace and an oil-fired hot water heater when the existing chimney flue is not of adequate size to accommodate both appliances is allowed. The chimney must be lined. This is required when replacing an existing furnace or water heater when the chimney is not properly sized for both appliances.

Authority: 32 M.R.S.A. §2313, §2313-A, §2353, and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

# Chapter 13:	INSTALLATION OF WASTE OIL APPLIANCES AND WASTE OIL SUPPLY TANKS

Summary: The purpose of this Chapter is to provide requirements for the use of waste oil burning equipment and accessory equipment installations in specific applications. See Appendix A and B for further information.

13-1	NATIONALLY-ACCREDITED TESTING LABORATORY

All heating, chimney and/or fireplace equipment installed as well as any accessory equipment installed must be listed and approved by Underwriters’ Laboratories or by a nationally-accredited testing laboratory, with certification that applicable national and Maine standards have been met. Such listing must be in effect at the time of installation. All equipment must be continually listed by a nationally-accredited testing laboratory.

13-2	General

13-2.1	The installation of waste oil burning unit(s) and their service shall be performed by licensed individuals experienced in servicing and installing such equipment.

13-2.2	The installation and servicing of waste oil appliances shall be made in accordance with the manufacturer’s instructions and with state and local codes.

13-2.3	Waste oil tanks must be labeled with the words “Used Oil” in accordance with 40 CFR 279.22(c)(1-2).

13-3	Use of Approved Equipment

Waste oil burning equipment shall be listed or labeled by a nationally-accredited testing laboratory. Appliances and accessory equipment listed for a specific purpose shall be considered as meeting the requirements of NFPA #31 and other Rules adopted by the Board.

13-4	Type of Fuel

13-4.1	Waste oil fuel tank(s) may contain: 1 and 2 fuel oils; crankcase oil up to 50 SAE; automatic transmission fluid; and hydraulic oils; and specified refined waste fuels only. A complete definition of waste oil can be found in the Department of Environmental Protection’s Chapter 860: “Waste Oil Management Rules,” Section 4: “Identification of Waste Oil.”

13-4.2	Other types of liquids such as anti-freeze, cleaners, thinners, solvents, gasoline or additives, and any other types of hazardous materials may not be introduced into a waste oil supply tank.

13-5	Oil Supply Tank Arrangement.

13-5.1	All tanks serving a waste oil appliance shall conform to NFPA # 31 and this Chapter.

13-5.2	An exception to 13-5.1 provides that a waste oil supply tank of 660 gallons or two tanks of aggregate capacity, supplying a Waste Oil Appliance shall be installed with a receptacle or funnel used specifically for introducing waste oils into a specifically marked waste oil supply tank when the tank and accessories have a 2 inch diameter (nominal inside diameter) iron pipe vent to the outside of the building or structure.

13-5.3	The arrangement of the waste oil tank recovery receptacle shall comply with the following:

13-5.3.1	The recovered waste oil shall be introduced into the supply tank manually through a valved recovery pan or funnel for waste oils only and shall be located at the top of the tank. See Figure 4(a). The receptacle to receive the oils may be installed as follows:

13-5.3.2	Install a close x 2 inch threaded (NPT) metal nipple in the oil supply tanks’ 2 inch access opening;

13-5.3.3	Install the receptacle (funnel, pan, catch basin, etc.) at the top of the valve;

13-5.3.4	Install a gauge in the other available access opening of the tank;

13-5.3.5	Spillage by individuals pouring recovered waste oil from a pan, catch basin, or other type of recovery container, must be minimized by metal steps, corresponding to the height of the tank, so an individual does not have to reach beyond his or her shoulder level while transferring the fuel from the recovery container to the oil supply receptacle. Steps provided shall be a minimum of three (3) feet wide, with a tread height of not more than eight (8) inches. Ladders are not an acceptable alternative; and

13-5.3.6	Any spillage shall be cleaned up immediately and reported to the Department of Environmental Protection.

13-5.4	As an option to the tank arrangement in paragraph 13-5.2, and Figure 4(a), the tank arrangement may be supplied with a funnel and a fill and vent pipe extending to the outside, providing the fill point is identified by a metal placard attached to the building stating: “ Waste oil tank, check for inside valve closure prior to filling.” See Figure 4(b).

13-5.4.1	The waste oil supply tank in Figure 4(b) must be provided with a combination oil gauge and vent alarm at the vent pipe due to the availability of only three access openings in the tank. Waste oil tanks with four (4) access openings may use a separate gauge and vent alarm.

13-5.4.2	Spillage due to pouring recovered waste oil from a pan, catch basin, or other type of recovery container must be minimized by metal steps, corresponding to the height of the tank, so an individual does not have to reach beyond his or her shoulder level while transferring the fuel from the recovery container to the oil supply receptacle. Steps provided shall be a minimum of three (3) feet wide, with a tread height of not more than eight (8) inches. Ladders are not an acceptable alternative.

      - Any spillage shall be cleaned up immediately and reported to the Department of Environmental Protection.

Authority: 32 M.R.S.A. §2313, §2353, and §2402-A

02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

381		OIL AND SOLID FUEL BOARD

Chapter 15:	DENIAL APPEALS

Summary: This Chapter sets forth a licensee’s right to appeal certain board actions.

  - APPEAL OF LICENSE DENIAL

An applicant or licensee may appeal a license denial to the Board by filing a request for hearing with the Board in writing within 30 days of the applicant’s or licensee’s receipt of notice of the denial. An adjudicatory hearing will be scheduled upon receipt of a timely appeal. Non-timely appeals will be denied without hearing.

AUTHORITY: 5 M.R.S.A. §9051

Appendix A

DEPARTMENT OF ENVIRONMENTAL PROTECTION

OIL REGULATIONS

The Department of Environmental Protection's Bureau of Remediation and Waste Management regulates underground oil storage tanks and the clean up of any discharge of oil onto or into land or waters of the State of Maine.

1.	Underground Oil Storage Tanks:

All underground oil storage tanks must be installed by a person who is licensed by the Board of Underground Storage Tank Installers. The installation and operation of the tank is regulated by the Department of Environmental Protection.

2.	Reporting Oil Spills:

To avoid fines or civil penalties, oil spills onto or into the lands or waters of the State of Maine must be reported within 2 hours to the Department of Environmental Protection. To report a leak, call the 24 hour response line at 1-800-482-0777.

3.	Abandonment of Tank by Removal:

Tanks must be disposed of in accordance with the Department of Environmental Protection Rules. Used, underground, oil storage tanks are prohibited from use for aboveground supply of oil except where a Maine registered engineer certifies that the tank meets the requirements of UL 142 and NFPA 30.

4.	Underground Piping and Aboveground Tanks with Over 660 Gallons or Aggregate Volume Over 1320 Gallons

If underground or under-slab piping is to a tank of over 660 gallons capacity or to tanks with an aggregate capacity of over 1320 gallons, then the installation of the underground piping must be installed by a certified underground oil tank installer.

A.	Piping must be installed by a certified underground oil tank installer as required under 38 MRSA §570-K, Above ground oil storage facilities.

B.	Piping must be constructed of fiberglass, cathodically protected steel, or other equally noncorrosive material approved by the Department of Environmental Protection as required under Chapter 691, Rules for Underground Oil Storage Facilities.

C.	Piping installed on or after June 24, 1991 must include secondary containment and leak detection as required under Chapter 691, Rules for Underground Oil Storage Facilities.

D.	Piping that is “grouted,” such as piping run on the surface of a floor and then encased in grout or cement or some similar material, shall be considered underground piping. Such grouted piping must include secondary containment and leak detection as required under Chapter 691, Rules for Underground Oil Storage Facilities.

5.	For more information about the Department of Environmental Protection’s regulations, contact them at:

Maine Department of Environmental Protection

Bureau of Remediation and Waste Management

17 State House Station

Augusta, Maine 04333

(207) 287-2651

Appendix B

CHAPTER 425

DEPARTMENT OF ENVIRONMENTAL PROTECTION

Asbestos Regulations

The Department of Environmental Protection's Bureau of Remediation and Waste Management regulates the handling of friable asbestos in the State of Maine. It is also regulated by the Federal Occupational Safety and Health Administration (OSHA).

Friable asbestos is material containing asbestos that is loose, crumbly, or can otherwise easily give off fibers and non-friable material that is processed and becomes loose or crumbly. Asbestos used on boilers, pipes, and tape on air ducts is friable.

The state certifies individuals and licenses companies that work with asbestos. It also sets standards for handling and disposing of asbestos. Anyone impacting more than three square feet or three linear feet of asbestos must be certified and licensed by the DEP, except that licensed oil burner technicians are exempt from certification and licensing requirements when conducting an emergency repair, installation, removal or servicing of heating equipment in single-family homes. An emergency is defined to include: a sudden, unexpected event that, if not immediately attended to, presents a safety or health hazard; operations necessitated by non-routine failures of equipment or to protect equipment from damage; and actions of fire and emergency medical personnel pursuant to duties within their official capacities. However, the oil burner technicians who are exempt from certification and licensing are still required to comply with all of the notification, handling, and disposal requirements.

For more information about the asbestos regulations, including a list of licensed contractors and disposal facilities, contact:

Asbestos Unit, Coordinator				287-2651

Maine Department of Environmental Protection

Bureau of Remediation and Waste Management

17 State House Station

Augusta, Maine 04333

Occupational Safety and Health Administration		622-8417

40 Western Avenue

Augusta, Maine 04330

In addition, the Safety Division of the Maine Bureau of Labor Standards offers free consultations. Contact them at:

Safety Division						624-6460

Bureau of Labor Standards

82 State House Station

Augusta, Maine 04333

Appendix C

MEMORANDUM OF UNDERSTANDING BETWEEN THE OIL AND SOLID FUEL BOARD AND THE PLUMBERS’ EXAMINING BOARD FOR THE

INSTALLATION OF HOT WATER OR STEAM & WARM AIR HEATING SYSTEMS

RADIATION SUPPLY AND RETURN CONNECTIONS

ALL TASKS TO BE PERFORMED UNDER THE SUPERVISION

AND RESPONSIBILITY OF A LICENSED MASTER OIL BURNER TECHNICIAN.

A Master Plumber; or a Journeyman Plumber, under the employment or direction of a Master Plumber,

SHALL NOT

1.	Pipe oil tank or run pipe from tank to oil burner.

2.	Install any electric wiring unless he or she is licensed to do so.

3.	Install any safety equipment.

4.	Install smoke pipe.

5.	Install thermostat and relays.

A Master Plumber; or a Journeyman Plumber, under the employment and direction of a Master Plumber,

MAY INSTALL

1.	Radiation, supply mains and returns, fittings, vents, gate valves, ball valves, zone valves, check valves or other valves that apply directly to the mechanical function of the heating system. This section does not apply to Safety Valves.

2.	Connect mains and returns to boiler.

3.	Connect make-up water to boiler.

4.	Install back flo preventer.

5.	Connect tankless water heater.

A Master Plumber or a Journeyman Plumber, holding an Apprentice Oil Burner license; under the direct supervision of a Master Oil Burner Technician,

##### MAY

1.	Set boiler.

2.	Set warm air furnaces, install plenums, warm air and return ducts, registers and piping.

A Master Oil Burner Technician or Solid Fuel Master, as appropriate; or

A Journeyman Burner Technician, under the indirect supervision of an appropriate Master; or

An Apprentice Oil Burner or Solid Fuel Technician, under the direct supervision of an appropriate Master or Journeyman,

MAY

1.	Set boiler.

2.	Pipe radiation, vents, valves, etc.

3.	Install mains and returns.

4.	Connect mains and returns to boiler.

5.	Connect make-up water to boiler.

6.	Install back flo preventer.

7.	Install and pipe oil tank.

8.	Install set pump, if necessary.

9.	Connect oil piping to boiler.

10.	Install smoke pipe.

11.	Install safety equipment to include safety valves.

12.	Install thermostats and relays.

13.	Install electric wiring to a breaker or fuse box.

14.	Connect a tankless water heater within the boiler room or, if not enclosed, with 15' horizontally to the nearest branch water supply.

Date: April 3, 1991						Date: April 3, 1991

Lloyd Rainey, Chairperson					James Carey, Chairperson

Plumbers’ Examining Board					Oil and Solid Fuel Board

Appendix D

MEMORANDUM OF UNDERSTANDING BETWEEN THE OIL & SOLID FUEL BOARD AND THE PROPANE AND NATURAL GAS BOARD

FOR THE INSTALLATION OF HOT WATER OR STEAM HEATING SYSTEMS

ALL TASKS TO BE PERFORMED UNDER THE SUPERVISION AND RESPONSIBILITY OF A LICENSED MASTER OIL BURNER TECHNICIAN

A Propane and Natural Gas Appliance Connection and Service Technician licensed by the Propane and Natural Gas Board with an Apprentice Oil Burner Technicians License

MAY:

- Set oil-fired boiler.

- Pipe radiation, vents, valves, etc.

- Install mains and returns to boiler.

- Connect make up water to boiler.

- Install backflow preventer.

- Install electric wiring to a breaker or fuse box, including emergency switch, service switch and thermo fireomatic switch (per Electricians’ Examining Board Rules).

- Connect a tankless or indirect fired water heater within the boiler room or, if not enclosed, with 15’ horizontally to the nearest branch water supply.

- Install safety devices that are not oil specific.

A Propane and Natural Gas Appliance Connection and Service Technician licensed by the Propane and Natural Gas Board

SHALL NOT:

- Pipe or set oil tank or run oil line from tank to burner.

- Install any safety controls that are oil specific.

- Install any flue pipe or tie appliance into chimney.

- Shall not fire or adjust the heating appliance.

ALL TASKS TO BE PERFORMED UNDER THE SUPERVISION AND RESPONSIBILITY OF A LICENSED PROPANE AND NATURAL GAS APPLIANCE CONNECTION AND SERVICE TECHNICIAN

A Master or Journeyman Oil Technician licensed by the Oil and Solid Fuel Board with a Propane and Natural Gas Helpers License

# MAY:

- Set propane or natural gas fired boilers.

- Pipe radiation, vents, valves, etc.

- Install mains and returns to boiler.

- Connect make up water to boiler.

- Install backflow preventer.

- Install electric wiring to a breaker or fuse box, including service switch (per Electricians’ Examining Board Rules).

- Connect a tankless or indirect fired water heater within the boiler room or, if not enclosed, with 15’ horizontally to the nearest branch water supply.

- Install safety devices that are not propane and natural gas specific.

A Master or Journeyman Oil Technician licensed by the Oil and Solid Fuel Board

# SHALL NOT:

- Pipe or set propane tank or run propane or natural gas lines to burner.

- Install any safety controls that are propane and natural gas specific.

- Install any flue pipe or tie appliance into chimney.

- Shall not fire or adjust the heating appliance.

Date:	January 17, 2001					Date: January 25, 2001

Alan Landeen, Chairperson					James Carey, Chairperson

Propane and Natural Gas Board				Oil and Solid Fuel Board

Appendix E

MEMORANDUM OF UNDERSTANDING BETWEEN THE OIL & SOLID FUEL BOARD AND THE ELECTRICIANS’ EXAMINING BOARD

#### FOR THE INSTALLATION, SERVICE AND REPAIR

OF HOT WATER, STEAM, WARM AIR HEATING SYSTEMS AND

OIL FIRED HOT WATER HEATERS

A person holding a valid State of Maine Oil Burner Master or Journeyman Technician’s license may install electrical conductors, including the branch circuit, fittings, devices and raceways for the power and control of hot water, steam, warm air heating systems and oil fired water heaters. The technician may also install, replace or adjust any motor or control on the heating branch circuit as required by the NEC 422-12, 1999 edition. This also applies to the branch circuit supplying the oil fired hot water heater.

The technician may install the branch circuit overcurrent device, provided a space in the electrical panel is available. The technician may also install the associated low voltage wiring provided its power supply is fed from the heating branch circuit.

This does not include the wiring of unit and kick space heaters not associated with the heating branch circuit. This does not allow the technician to install receptacles and lighting for servicing the equipment or to wire air conditioning units, evaporators and condensers.

All electrical installations performed must meet the requirements of the National Electrical Code (NFPA 70).

Date:	February 16, 2001					Date: February 21, 2001

Brian McDougal, Chairperson					James Carey, Chairperson

Electricians’ Examining Board					Oil and Solid Fuel Board

Appendix F

STATE OF MAINE

EMERGENCY CHIMNEY UPDATE

WAIVER FORM

Dear Consumer: The State of Maine, Oil & Solid Fuel Board adopted the National Fire Protection Association (NFPA) standard # 31 (1997 edition) which requires that, before an existing oil fired appliance is replaced with a new appliance, the chimney to which it is connected must be lined with an approved lining system. This regulation is intended to protect you, the consumer.

When an emergency situation arises that does not allow adequate time to get the chimney lined and/or repaired before installing the new heating appliance, the licensee may grant a waiver of up to ninety (90) days to make required repairs. It is the licensee’s responsibility to ensure that the installation meets all standards adopted by the Board and the manufacturer’s instructions. The licensee must either install or have installed the required liner or make the proper repairs within the 90 day time period. In cold weather an emergency situation may include, but is not limited to, situations of serious equipment failure, such as a cracked heat exchanger of a warm air furnace or a leaking boiler. Emergency situations may also include failure of equipment that generates hot water, and the unavailability of a chimney professional.

A copy of this waiver must be provided to the building owner and the Oil and Solid Fuel Board.

### INSTALLER INFORMATION

| Name of Installer: |
| --- |
| D/B/A |
| Mailing Address: |
| City: | State: | Zip Code: |
| County: | Home Telephone: (________)___________-_______________ Work Telephone: (________)___________-_______________ |
| By my signature, I certify that I will follow-up within ninety (90) days to ascertain if the liner has been installed. Signature of Installer: ____________________________________________Date:____________________________ |

### CONSUMER INFORMATION

| Consumer’s Name: |
| --- |
| Mailing Address: |
| City: | State: | Zip Code: |
| County: | Home Telephone: (________)___________-_______________ Work Telephone: (________)___________-_______________ |
| By my signature, I certify that I am aware that, if I do not get my chimney lined, I may be in violation of State of Maine Law, 32 M.R.S.A. Chapter 33 and a State of Maine Oil and Solid Fuel Board Compliance Officer may contact me. Signature of Consumer: ____________________________________________Date:__________________________ |

APPENDIX G

STATE OF MAINE

CHIMNEY OR FIREPLACE CONSTRUCTION/INSTALLATION DISCLOSURE

Dear Consumer: As of January 1, 1992, State law, specifically 32 M.R.S.A. §2313-A, requires that chimney or fireplace installers provide you with this “Disclosure” prior to the installation or construction of your chimney or fireplace. The purpose of this Disclosure is to inform you that the National Fire Protection Standard #211 (NFPA #211) is the current standard which applies to all new construction of chimneys and fireplaces. Please note that the State of Maine does not require registration or licensure of chimney or fireplace installers. It is important to realize that many fires are caused each year from improperly constructed fireplaces and chimneys. This disclosure form should help you in making an informed decision as to the abilities of the installer and under what requirements the installation must comply.

INSTALLER INFORMATION

| Name of Installer: | D/B/A: |
| --- | --- |
| Name of Installer (if incorporated): | D/B/A: |
| Legal Address: |
| City: | State: | Zip Code: |
| County: | Home Telephone: (_____)________-____________ Work Telephone: (_____)________-____________ |
| Years of experience doing fireplace or chimney installations: |

CONSUMER INFORMATION

| Name of Consumer: |
| --- |
| Mailing Address: |
| City: | State: | Zip Code: |
| County: | Home Telephone: (_____)________-____________ Work Telephone: (_____)________-____________ |

Installer, please give a brief description of installation being offered: __________________________

I hereby attest that the preceding information provided is true to the best of my knowledge. I also understand that if I fail to conform with the standards as outlined in NFPA #211 that I shall be subject to penalties as outlined in Title 32, M.R.S.A., Chapter 33 and the Oil and Solid Fuel Board Rules.

Signature of Installer: _________________________________	Date: ______________________