## Abbreviations
Abbreviation | Long Version
ACBM | Asbestos Containing Building Material
ASHRAE | American Society of Heating, Refrigeration, and Air-Conditioning Engineers.
BFI | Bureau of Financial Institutions
BMV | Bureau of Motor Vehicles
BVS | Bureau of Veterans' Services
CDS | Child Development Service
CETA | Comprehensive Employment and Training Act
CSOB | Crosss State Office Building
DACF | Department of Agriculture, Conservation, and Forestry
DDPC | Dorothea Dix Psychiatric Center
DEP | Department of Environmental Protection
DHHS | Department of Health and Human Services
DMR | Dpartment of Marine Resources
DOC | Department of Corrections
DOL | Department of Labor
DPFR | Department of Professional and Financial Regulation
DPS | Department of Public Safety
IF&W | Inland Fisheries & Wildlife
IPM | Integrated Pest Management
EMDC | Eastern Maine Development Corporation
GBSD | Governor Baxter School for the Deaf
HETL | Health and Enviornmental Testing laboratory
HR | Human Resources
IAQ | Indoor Air Quality
LBP | Lead Based Paint
LUPC | Land Use Planning Commission
MCC | Maine Correctional Center
MCJA | Maine Criminal Justice Academy
MCPDS | Maine Commission on Public Defence Services
MECDHH | Maine Educational Center for the Deaf and Hard of Hearing
MFS | Maine Forest Service
MPUC | Maine Public Utilities Commission
MSL | Maine State Library
NRSC | Natural Resource Service Center
OCFS | Office of Child and Family Services
OCME | Office of the Chief Medical Examinter
OCP | Office of Cannabis Policy
OFI | Office for Family Independence
OIT Print Room | Office of Information Technology
OMAG | Office of the Maine Attorney General
OSA | Office of the State Auditor
PDC | Planning, Design, and Construction
PMD | Property Mangement Division
SESC | Security and Employment Service Center
SOS | Secretary of State
TSI | Thermal System Insulation

## 2022
Date Initiated | Building | Agency | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date SES Onsite | SES Rpt Date | IEP Name | IEP Rpt Date | Remediator Name | Outcome
2022-05-09 | Gardiner Annex | DPFR | Exam Div & Susi Office | Leased | DPFR / Exam Division & Mark Susi Office | 76 Northern Ave | Gardiner | Mold | Address water damage & mold issues | NA | NA | AQM | 2022-05-20 | Servpro | Areas successfully remediated
7/5/2022* | CSOB | SOS | HVAC Diffuser Mold | Owned | 4th Flr SOS Area (only) | 111 Sewall St | Augusta | IAQ & Mold | Remediate areas / issues based on AQM report | NA | NA | AQM | 2022-06-06 | Servpro | Diffusers and ceiling tiles cleaned and flex-ducts replaced
2022-06-30 | 221 State St | HETL | Idexx Break Room | Owned | HETL - Idexx Break Rm | 221 State St | Augusta | IAQ & Mold, Asbestos | Address IAQ complaints; follow-up for asbestos flooring found by AQM | 2022-07-12 | NA | AQM | 2022-07-18 | Atlantic Env | Flooring removed by licensed abatement contractor
7/6/2022* | CSOB | Multiple | HVAC Diffuser Mold | Owned | Floors 1-7 | 111 Sewall St | Augusta | IAQ & Mold | Determine occurrence and extent of mold on diffusers and flex duct | 7/7/2022 - 8/10/22 | 7/11/22 - Flr3, 11/4/22 Flr 1-7 | NA | NA | Servpro | Diffusers and ceiling tiles cleaned throughout the building by Servpro; completed in Dec 2024
2022-07-07 | Cultural Bldg |  | Library Carpet | Owned | Library / Flr-2 | 230 State St | Augusta | Mold / Bacteria | Assess carpet for mold contamination following roof leak | 2022-07-08 | 2022-07-12 | None | NA | Servpro | Carpet removed and area cleaned by Servpro
2022-07-14 | Crime Lab | DPS | Storage Rooms | Owned | Storage Rooms / Old Drying Lockers | 26 Hospital St | Augusta | Mold | Determine extent and cause of mold growth in Storage Rm / Lockers | 7/15/22, 7/18/22 | 2022-07-20 | AQM | 2022-07-23 | Servpro | Area successfully remediated and cleaned. PMD asked to replaced lower walls that were removed
2022-07-14 | Nash School | SOS | Odor | Owned | 1st and 2nd Floors | 103 Sewall St | Augusta | Odor | Identify source of sewer-like odor | 7/26/22 - 8/2/22 | NA | NA | NA | Building Control | Odor source location narrowed by SES; final ceiling cut by PMD found detached vent pipe; fixed by PMD
2022-07-20 | Benton Ranger Station | MFS | Asbestos | Owned | Dept of Agriculture, Maine Forest Service | 57 Bangor Rd | Benton | Asbestos | Coordinate asbestos flooring abatement | NA | NA | Atlantic Env | 2022-07-20 | RJ Enterprises | Flooring removed by licensed abatement contractor
7/18/2022* | Gardiner Annex | DPFR | IAQ | Leased | DPFR / Whole Building | 76 Northern Ave | Gardiner | Mold, Asbestos | Assess IAQ issues / risks throughout building | 7/20/2022 (Mold), 8/4/22 (Humidity), 8/30/22 (Ceiling) | 7/22/22 (Mold), 8/9/22 (Humidity), 9/8/22 (Ceiling) | AQM | 7/20/2022 (for Landlord), 9/14/22 Carpets | Servpro | All mold and asbestos remediated by summer / fall 2023; Substantial renovations done throughout building to prevent future issues
2022-07-20 | PMD Service Bldg | PMD | IAQ | Owned | BGS Property Management | 15 Columbia St | Augusta | Mold & Asbestos | Employee concern for new work area (general concern due to their own sensitivity) | 2022-07-21 | NA | NA | NA | NA | Employee assignment did not go through; request withdrawn
2022-07-25 | DHHS-Skowhegan | DHHS | OFI | Leased | OFI / Old OFI Area | 98 North Ave | Skowhegan | Mold | Assess employee complaints of IAQ concerns / allergy symptoms | 2022-07-27 | 2022-08-02 | AQM | 2022-08-15 | Servpro | All air-supply vents cleaned; all affected areas deep cleaned (by Servpro)
2022-07-25 | Cony Road Building |  | General Walkthrough | Owned | General | 333 Cony Rd | Augusta | General | Simple participation in walkthrough for any future work requested | 2022-07-26 | NA | NA | NA | NA | SES will assist with any new / future requests
2022-07-27 | CETA | Vacant | Pre-Renovation Inspection | Owned | All Areas | 27 Independence Dr | Augusta | Mold / Lead / Asbestos | Inspection to determine potential exposures to renovation personnel | 2022-08-05 | 2022-08-17 | AQM | 2022-08-17 | NA | Prior reports of lead and asbestos reviewed. BGS & AQM Reports provided to IF&W for their use; BGS role complete
2022-08-05 | 161 Capitol St |  | Asbestos File Cabinets | Leased | Board of Medicine | 161 Capitol St | Augusta | Asbestos | Remove and dispose of 5 asbestos-containing file cabinets | NA | NA | AQM | 2022-08-22 | Atlantic Env | All cabinets removed by a licensed abatement contractor
2022-08-10 | CSOB | Multiple | Men's Room Water Leak | Owned | 1st Flr, 2nd Flr | 111 Sewall St | Augusta | Dryout, Mold | Coordinate drying after water damage and mold remediation in small areas | 2022-08-11 | NA | NA | NA | Servpro | Affected walls either removed or dried in a timely manner; PDM replaced building materials
2022-08-22 | Key Plaza | DHHS | 8th & 9th Floors Water Infiltration | Leased | DHHS / 8th & 9th Floors | 286 Water St | Augusta | Mold | Assess water infiltration (through façade) and possible mold | 8/24/22, 8/31/22, 10/17/22 | 2022-09-12 | Haley Ward | 2023-07-17 | Servpro | Assessment completed by Fall 2023. BGS agreed to remediation scope from Lessor's consultant. Remediation Pending
2022-08-30 | Tyson | DOC | Falling Ceiling Paint | Owned | DOC / 3rd Floor | 25 Tyson Dr | Augusta | Lead | Determine if paint falling from ceiling poses a lead-exposure risk | 2022-09-01 | 2022-09-06 | NA | NA | NA | A Full Hazardous Materials Survey was conducted in 1998 by Facility Management Group, Inc. and found no lead in the ceiling paint
2022-08-31 | Key Plaza | DHHS | 3rd Floor Cracked Roof Drain | Leased | DHHS / 3rd Floor | 286 Water St | Augusta | Mold | Assess impact to wall system from leak in roof drain | 2022-08-31 | 2022-08-31 | NA | NA | Advance-1 | Remediation successful; PRV test passed
2022-09-01 | CSOB | Multiple | Roof Drain Leak | Owned | 5th, 4th and 3rd Floors | 111 Sewall St | Augusta | Mold | Assess impact to walls of columns from leak in roof drain | 2022-09-01 | 2022-09-02 | NA | NA | Servpro | All PRV Tests passed; remediation not needed on 3rd Floor
2022-09-07 | 221 State St | DPFR | 2nd Floor IAQ | Owned | Areas to be occupied by DPFR | 221 State St | Augusta | IAQ, Mold, Asbestos, Lead | Assess any IAQ concerns prior to occupation by DPFR | 10/4/2022, 10/7/22, 10/11/22 | NA | AQM | 2022-10-19 | Servpro | All relevant areas cleaned; visual inspection revealed well-cleaned surfaces / areas
2022-09-08 | Harlow Bldg |  | Roof Leak - LUPC | Owned | DACF, 4th Floor Reception in LUPC | 18 Elkins Ln | Augusta | Mold | Assess water impact to ceiling and carpet in Room 413 | 2022-09-09 | NA | AQM | 2022-09-15 | Octagon | All PRV Tests passed
2022-09-19 | 221 State St | HETL | Room 114 Sink Leak | Owned | HETL - Shipping & Receiving | 221 State St | Augusta | Mold | Assess damage to sink cabinet | 2022-09-20 | 2022-09-20 | NA | NA | Servpro | Sink dried & isolated, as occupants will be moving out of the building in several weeks
2022-09-29 | Deering |  | Room 128 Musty Odor | Owned | DOE / Child Nutrition (Room 128) | 90 Blossom Ln | Augusta | Odor (Mold) | Determine source of musty odors | 2022-09-30 | 2022-10-06 | NA | NA | BGS / PMD | PMD will install air-exchanger and set up air-barrier in tunnel to remove / block musty odors
2022-09-29 | 85 Leighton Rd | OIT | Printer Toner | Leased | OIT / Print Room | 85 Leighton Rd | Augusta | Chemical / Particulate | Assess surface contamination from printer toner; coordinate cleaning & prevention | 2022-10-07 | 2022-10-17 | NA | NA | Octagon | HVAC system cleaned; All Print Room surfaces / areas detail-cleaned
2022-10-03 | PMD Service Bldg | BGS | Dust Concern | Owned | Building Control / Door D10 Entry | 15 Columbia St | Augusta | Asbestos & Lead | Assess concern over dust on floor after drilling into ceiling | 2022-10-03 | NA | NA | NA | NA | No risks present; Building Control notified by email (10/3/22)
2022-10-04 | Records Center |  | Mercury Spill | Leased | Warehouse Archives / Records Room | 10 Water St | Hallowell | Mercury | Mercury cleanup in the Records Room | 10/21/22, 10/24/22 | 2022-10-31 | Maine DEP Response | 2022-10-04 | US Ecology | Haley Ward determined that mercury was satisfactorily cleaned and no risks remain
2022-10-06 | Mechanical Building | BGS | Musty Odor | Owned | 1st Flr Elevator Lobby | 54 Independence Dr | Augusta | Odor (Mold) | Determine cause of odor | NA | NA | NA | NA | NA | Staff reported that adding water to floor traps solved the problem.
2022-10-07 | Norridgewock Ranger Station | MFS | Asbestos Flooring | Owned | All Areas | 564 Skowhegan Rd | Norridgewock | Asbestos | Test flooring for asbestos | NA | NA | AQM | 2022-10-18 | Octagon | All Clearance testing passed
2022-10-07 | CDS-Skowhegan | CDS | Odor Complaints | Leased | Entry, Kitchen areas | 16 Madison Ave | Oxford | Odor | Inspect areas with mold odor (Entry) and other odor (Kitchen / general) | 2022-10-12 | 2022-10-25 | NA | NA | NA | No issues in Entry. Rodent issues throughout especially in Kitchen area
2022-10-12 | State House |  | Attic Sprinkler Leak | Owned | 4th, 3rd, 2nd and 1st Floors | 210 State St | Augusta | Mold | Identify materials still wet following sprinkler leak (10/6/22) | 2022-10-13 | 2022-10-13 | AQM | 2022-11-08 | Servpro | Testing did not reveal any abnormal or concerning mold levels in the affected areas; materials verified as dry
2022-10-13 | MCC-Windham | DOC | Asbestos Investigation | Owned | Several Buildings as requested by involved SOM parties | 17 Mallison Falls Rd | Windham | Asbestos | Re-check roof and windows on several buildings that could not be accessed prior | 2022-10-25 | NA | AQM | 2022-10-30 | Envirovantage | AQM Report received and sent to involved parties
2022-10-17 | Crime Lab | DPS | Garage Bay 3 Mold | Owned | Garage Bay 3 | 26 Hospital St | Augusta | Mold | Assess mold on walls in Garage Bay 3 | 10/18/22, 11/1/22 | NA | NA | NA | Octagon | Wall systems remediated and cleaned successfully
2022-10-25 | CSOB | SOS | 6th Floor Roof Leak | Owned | 6th Floor / Attorney General | 111 Sewall St | Augusta | Odor (Mold) | Assess water impact from ceiling leak at Alma Zachary's cubicle | 2022-10-26 | 2022-10-26 | NA | NA | NA | No significant mold; request submitted to repair roof leak and replace 3 cubicle walls
2022-11-01 | DHHS-Winthrop | DHHS | Flooring Renovation | Leased | Room 132 (Jordan's Office) | 1705 US Route 202 | Winthrop | Asbestos | Onsite consult for 9x9 floor tiles damaged when pulling up carpet | 2022-11-01 | NA | Acadia Contractors | Unknown | NA | BGS asked to consult; advised to stop pulling carpet and have tiles tested
2022-11-01 | 7 Chimney Loop | DEP | IAQ Concerns | Owned | DEP Response Offices | 7 Chimney Ln | Augusta | Mold | Inspect areas requested by Jon Woodard | 2022-11-01 | 2022-11-10 | NA | NA | Servpro | Area successfully remediated and cleaned. PMD asked to replaced lower walls that were removed
2022-11-01 | 264 Civic Ctr Dr | DOL | Storage Humidity | Leased | Basement Storage Area | 264 Civic Center Drive | Augusta | Mold | Inspect and advise regarding excess humidity in Storage Area | 2022-11-08 | NA | NA | NA | NA | SES advised DOL on humidity control; directed to consult Servpro for proper dehumidifiers to use
2022-11-03 | Blaine House |  | 2nd Floor Window Painting | Owned | 2nd Floor, several rooms | 192 State St | Augusta | Lead | Assess potential worker exposure to lead during painting | NA | 2022-11-18 | NA | NA | NA | Determined that workers will be safe (without PPE) during painting as-described in scope
2022-11-09 | MCC-Windham | DOC | Asbestos New Finding | Owned | Tunnel Walls | 17 Mallison Falls Rd | Windham | Asbestos | Test black mastic found on exterior foundation walls of tunnels | NA | NA | AQM | 2022-11-14 | Envirovantage | All samples negative; results conveyed to remediation contractor and agency
2022-11-28 | MCC-Windham | DOC | Asbestos New Finding | Owned | Administration Security E and the Gymnasium | 17 Mallison Falls Rd | Windham | Asbestos | Test mastic found behind brick façade | NA | NA | AQM | 2022-12-05 | Envirovantage | All samples Positive; results conveyed to remediation contractor and agency
2022-11-28 | 19 Union St | OCP | Moldy Ceiling Tiles | Owned | Office of Cannabis Policy | 19 Union St | Augusta | Mold | Inspect several areas with water-stained / moldy ceiling tiles | 2022-11-29 | 12/2/22 (email) | NA | NA | BGS / PMD | SES Removed moldy ceiling tiles; PMD to replace
2022-11-28 | Bolton Hill HQ | DEP | Asbestos Flooring | Owned (Agency) | Duty Room | 2870 North Belfast Ave | Augusta | Asbestos | Assess asbestos content for floor tiles in a small area where the tiles are damaged | NA | NA | AQM | 2022-12-08 | DEP | Only a very small area (a couple of tiles) was damaged and below regulatory level. Removed by DEP as a courtesy
2022-12-05 | 7 Chimney Loop | DEP | Ceiling Mold | Owned | Response Training Room | 7 Chimney Loop | Augusta | Mold | Determine cause of mold; provide remedial recommendations | 2023-01-10 | 2023-01-27 | NA | NA | Octagon | Ceiling previously tested by AQM. Ceiling cleaned by Octagon and re-painted by PMD
2022-12-09 | DOC-Lewiston | DOC | Particulate Issue | Leased | All 1st Floor DOC space | 198 Maine St, Suite A | Lewiston | IAQ / Particulates | Assess employee health issues and reports of particulates on office surfaces | 12/13/22, Multiple through Feb 2023 | 2023-01-05 | NA | NA | Octagon. Knowles Mechanical | Work surfaces detail-cleaned; HVAC cleaned; HVAC cabinet cleaned after fiberglass removal, remaining fiberglass encapsulated
2022-12-20 | Merrill-Smith | MCPD | IAQ Test | Owned | Merrill (and common) Only, 1st and 2nd floor, not Attic or Basement | 187-189 State St | Augusta | IAQ & Mold | Pro-active test requested prior to occupancy | 2023-01-17 | NA | AQM | 2023-01-24 | PMD | AQM found only a dust issue; PMD was guided in cleaning practices and conducted the deep-cleaning

## 2023
Date Initiated | Building | Agency | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date BGS Onsite | BGS Rpt Date | IEP Name | IEP Rpt Date | Remediator Name | Outcome
2023-01-20 | Marquardt | NRSC | 2nd Floor Sewer Odor | Owned | NRSC - South End / 2nd Floor | 32 Blossom Ln | Augusta | Odor | Determine Source of Sewer Odor | 2023-01-25 |  | NA | NA | PMD | PMD found and capped several open pipes
2023-01-31 | Elkins |  | 3rd Floor Roof Leak | Owned | 3rd Floor Hall by Rooms 314-319 | 19 Elkins Ln | Augusta | Mold | Determine water damage and cause of musty odor | 2023-02-01 | NA | NA | NA | PMD | Impacted walls are plaster and brick; only potential odor is from ceiling tiles, removed (2/1/23) by PMD
2023-01-27 | 1037 Forest Ave |  | Water Damage & Mold | Leased | Worker's Comp | 1037 Forest Ave | Portland | Mold | Advise Agency on recent water intrusion and presence / exposure to mold | NA | NA | AQM | 2023-01-28 | NA | Lessor was not cooperative; advised Agency through the process to break lease and relocate
2023-02-05 | Marquardt | DMR | Sprinkler Freeze | Owned | 1st and 2nd Floor | 32 Blossom Ln | Augusta | Dry-out | Coordinate material removal and dryout in timely manner | 2023-02-06 | NA | NA | NA | Servpro | Materials removed and remaining systems dried in timely manner to prevent mold growth (verification not necessary)
2023-02-05 | DHHS-Lewiston | DHHS | Sprinkler Freeze | Leased | DHHS, Mezzanine and 1st Floor | 200 Main St | Lewiston | Dry-out | Assess water impact and mold potential; assign AQM for testing; Multiple inspections and testing required | 2023-02-09 | NA | AQM |  | Servpro (NJ) | Lessor eventually achieved satisfactory remediation state after several re-inspections and demands for compliance
2023-02-06 | Marquardt |  | Milk Lab Ice Maker Leak | Owned | Milk Lab (1st Floor) | 32 Blossom Ln | Augusta | Dry-out | Coordinate material removal and dryout in timely manner | NA | NA | NA | NA | Servpro | Materials removed and remaining systems dried in timely manner to prevent mold growth (verification not necessary)
2023-02-09 | MFS Central Region HQ | MFS | Asbestos Flooring | Agency-Owned | All Flooring | 87 Airport Rd | Old Town | Asbestos | Assess flooring for asbestos content prior to renovations | NA | NA | AQM | 2023-02-21 | NA | Tiles to be removed are negative. Linoleum tested positive but is not damaged and not planned for removal.
2023-02-14 | DHHS-Bangor | DHHS | Roof Leaks | Leased | All Areas (sporadic locations) | 19 Maine Ave | Bangor | Dry-out | Assess areas of water impact and risk of mold | 2/17/2023, 3/3/23 | 2023-03-08 | NA | NA | NA | Most carpets and walls were dry. Micro exam of lower walls showed no mold. DHHS staff finished drying some lower walls.
2023-02-16 | MPUC-Hallowell | MPUC | Groundwater | Leased | Crawlspace | 26 Katherine Dr | Hallowell | Mold | PUC concerned with possible electrical damage and mold growth in Crawlspace. Assess damage and work done by contractor hired by Lessor. | NA | NA | AQM | 2023-02-17 | Advance1 | Remediation done as recommended, clearance test passed.
2023-02-21 | Houlton Barracks | Dept of Public Safety | Asbestos Flooring | Owned | Emergency Communications office | 1 Darcie Dr # 202 | Houlton | Asbestos | Assess potential for damaged flooring to contain asbestos | NA | NA | NA | NA | NA | MPS provided original packaging for both the floor tiles and mastic; tiles marked as "No asbestos"; mastic asbestos-free based on current MSDS from manufacturer.
2023-02-23 | BMV-Scarborough | BMV | Roof-drain Leak | Leased | Station Area (central location) | 200 Expedition Dr | Scarborough | Mold | Assess area after drying and carpet replacement; also assess employee symptoms that occur when ceiling tiles are removed and ceiling left open | 2023-02-24 | NA | AQM | 2023-03-11 | Octagon | SES report issued requiring Lessor remediation (conducted and completed successfully). Additional employee concerns raised and assessed over several inspections. 2nd report issued requiring actions to address mold from long-term humidity and HVAC issues.
2023-02-28 | DHHS-Bangor | DHHS | Exhaust Odor | Leased | All areas | 19 Maine Ave | Bangor | Odor | Apply ASHRAE standard to situation of aviation exhaust entrainment to HVAC, to force Lessor to pay for charcoal filters | NA | NA | NA | NA | NA | SES email to Lessor 3/31/23; Lessor responded immediately with intention to take care of charcoal filters
2023-03-07 | BVS Admin Building | BVS | Suicide | Owned | Men's Restroom | 83 Stanley Rd | Springvale | Bloodborne Pathogen | Coordinate cleaning and sanitation in response to suicide by firearm | NA | NA | NA | NA | Crime & Death Scene Cleaning | Some Restroom lower wall and floor materials removed, surfaces successfully cleaned.
2023-03-15 | Tyson | DEP / DOC | Window Lead Paint | Owned | All 3 Floors, along perimeter walls | 25 Tyson Dr | Augusta | Lead | Assess impact following accidental paint chip dislodging from windows during cleaning | 2023-03-16 | NA | NA | NA | Servpro | Servpro deep-cleaned heating units under widows and floor surrounding the heating units (all 3 floors)
2023-03-24 | State House | Legislature | Room 410 Ventilation | Owned | Legislature / Room 410 | State House Station | Augusta | Ventilation | Assess occupant complaints of sleepiness and perceived, poor ventilation | 2023-04-14 | 2023-04-21 | NA | NA | PMD | Inspection revealed flaws in air-supply to Room. SES advised PMD, who then modified the ducts to provide proper air supply
2023-04-04 | MFS-Outbuildings | DACF | MFS Outbuilding Lead Paint | Leased | Outbuilding |  |  | Lead | Assess one or more outdoor vehicle storage bays for lead-based paint | NA | NA | NA | NA | NA | Project closed; agency request withdrawn
2023-04-07 | 221 State St | HETL | Asbestos | Owned | 1st Floor (Cubicle Area) Men's Restroom Closet | 221 State St | Augusta | Asbestos | Assess potential for asbestos in Closet | 2023-04-14 | 2023-04-14 | NA | NA | NA | No materials at risk for ACM except 2 boxes of stored 12x12 tiles, which were determined asbestos-free per manufacturer spec sheet
2023-04-12 | DEP Response | DEP | Room 141 Floor Tiles | Owned | DEP Response / Room 141 | 3 Chimney Loop | Augusta | Asbestos | Test floor tiles for asbestos (several loose tiles) | NA | NA | AQM | 2023-04-19 | NA | All samples were negative for asbestos - no actions required.
2023-05-01 | Deering | DACF | Roof Leak | Owner | DACF / Room 311 | 90 Blossom Ln | Augusta | Water Damage | Assess water impact from roof leak | 2023-05-02 | NA | NA | NA | NA | Only a very small wall area (several square inches) contained elevated moisture; advised employees to have custodian apply fan for another couple days.
2023-05-01 | CSOB | NA | Roof Drain Leak | Owned | 6th Floor down to 1st Floor | 111 Sewall St | Augusta | Water Damage, Mold | Assess extent of water impact, dry areas / materials and remediate any mold | 2023-05-01 | NA | NA | NA | Servpro | Servpro removed walls and dried all areas possible; One column remained wet spanning 6th to 3rd floor. Servpro removed column walls and associated mold under containment
2023-05-01 | Lamoine Barn | DMR | Roof Leaks | Owned | DMR / Offices | 22 Coaling Station Ln | Lamoine | Water Damage, Mold | Assess impact to building and employees and provide recommendations for remediation | NA | NA | AQM | 2023-05-15 |  | Assessment conducted by AQM and report issued to Agency (advised to avoid use of impacted areas). Remediation on hold pending building engineering assessment
2023-05-02 | Tech Services Garage | DEP | Roof Renovation | Owned | Exterior / Roof | 174 Hogan Rd | Bangor | Asbestos | Test roof shingles for asbestos prior to renovation | NA | NA | AQM | 2023-05-15 | NA | Asbestos is not present in roofing materials
2023-05-02 | CSOB | Attorney General | Window Leak | Owned | Attorney General / 7th Floor Room 748 | 111 Sewall St | Augusta | Water Damage, Mold | Assess impact from window leak | 2023-05-19 |  |  |  |  | Chronic damage to sheetrock surrounding window. Mold growth possible within wall cavity (no exposed mold). Remediation on hold until façade work complete (to prevent further water intrusion)
2023-05-03 | Greenlaw | HETL | Window Leaks | Owned | 1st Floor, 3rd Floor | 47 Independence Dr | Augusta | Water Damage | Assess water impact from window leaks in 2 locations | 2023-05-08 | 2023-05-09 | NA | NA | NA | All walls dry within 2 weeks with no visible mold. Determined wallboard is mold resistant. Test cut made in 1 wall (1st Floor) and mold growth not present on backside of wallboard
2023-05-04 | Key Plaza | DHHS | 4th Floor Water Infiltration | Leased | DHHS / 4th Floor NE Corner | 286 Water St | Augusta | Water Damage, Mold | Assess water impact to rooms in the NE corner | 2023-05-04 | 2023-05-04 | AQM | 2023-06-12 | Lessor | SES report issued with recommendations. AQM also tested and provide report. Lessor used Servpro to remediate. Clearance testing passed.
2023-05-04 | DHHS-Machias | DHHS | Mold | Leased | OCFS area | 38 Prescott Dr | Machias | Mold | Assess employee reports of health issues and water damage, and suspected mold in carpet | NA | NA | AQM | 2023-06-16 | Eastern Mold Remediation | AQM Inspected and provided report to address mold. Lessor addressed issues. Clearance test passed
2023-05-09 | Blaine House |  | Garage Painting | Owned | Garage | 192 State St | Augusta | Lead | Coordinate surface-prep and repainting (current paint is lead-based) | NA | NA | NA | NA | Servpro | SES consulted with several potential contractors and chose Servpro to remove loose paint and dust and to repaint. Project scheduled for early spring 2024.
2023-05-25 | MPUC-Hallowell | MPUC | IAQ Test | Leased | All areas / floors | 26 Katherine Dr | Hallowell | IAQ | Assess IAQ to address employee reports / concerns | NA | NA | AQM | 2023-06-15 | NA | IAQ Testing found no significant issues. SES met with Agency to explain results
2023-05-31 | CDS-Arundel | CDS | Preschool Water Damage | Leased | Preschool Wing | 39 Limerick Rd | Arundel | Water Damage / Mold | Assess area for water impact and potential mold. | 2023-06-08 | 2023-06-21 | NA | NA | Unknown | SES identified mold on some walls from past toilet overflow and mold in HVAC from humidity. Report sent to Lessor. Agency reported that Lessor addressed areas via a certified contractor and were satisfied with the work
2023-06-01 | Cultural Building |  | Mold May2023 | Owned | Museum / 4th Floor Small Temp Gallery | 230 State St | Augusta | ME | Assess water impact caused by Abatement Contractor on 5th Floor | 2023-06-02 | 2023-06-06 | NA | NA | Octagon | SES identified wet walls and mold in impacted areas on both floors. General Contractor for the larger, ongoing building project oversaw remediation. Clearance test passed
2023-06-07 | Marquardt | DEP | Room 377 Odor | Owned | Room 377 (north) | 32 Blossom Ln | Augusta | ME | Assess employee report of musty odor in the room | 2023-06-14 | NA | NA | NA | NA | There were no water-damage or mold issues found (SES inspection)
2023-06-08 | Jonesboro Office | DACF | Roof Renovation | Owned | Roof (back side) | 307 Whitneyville Rd | Jonesboro | ME | Sample the roof for ACM prior to renovation | NA | NA | AQM | 2023-07-05 | NA | Materials tested in the House and garage all tested negative for asbestos
2023-06-14 | F Building - DDPC | DDPC | Musty Odor | Owned | DOC / 2nd Floor | 102 Hogan Rd | Bangor | ME | Assess area of complaint for mold / musty odor | 2023-06-27 | 2023-06-30 | NA | NA | Unknown | SES inspection identified wet and moldy wall and flooring from plumbing leak. Report issued and handled by Lessor. Agency reported satisfactory resolution
2023-06-28 | 101 Hospital St | BMV | Musty Odor | Owned | BMV / License Information | 101 Hospital St | Augusta | Mold | Assess area of complaint for mold / musty odor | 2023-06-29 | 2023-06-30 | AQM | 2023-08-02 | Servpro | SES identified mold on air-supply diffusers. AQM testing found no airborne mold concerns. Servpro cleaned all diffusers and employee work areas
2023-07-07 | MCJA | DPS | Humidity/ Mold | Owned | Bldg A - A004 | 15 Oak Grove Rd | Augusta | Mold | Assess musty odors and mold on ceiling tiles | 2023-07-18 | 2023-07-20 | NA | NA | Servpro | Mold growth from humidity identified on most surfaces. Servpro removed ceiling tiles and deep-cleaned all areas.
2023-07-11 | DOC-Ellsworth | DOC | Building Assessment | Leased | All DOC areas | 412 High St | Ellsworth | HazMat | Assess general employee concerns for visible damage in some areas and assess building prior to new lease | NA | NA | AQM | 2023-09-10 | NA | DOC chose to break lease and relocate due to the extent of water and mold-related damages
2023-07-17 | Crime Lab | DPS | DNA Lab Humidity | Owned | DNA Lab | 36 Hospital St | Augusta | Mold / Water Damage | Assess condensation above ceiling and moldy ceiling tiles | 2023-07-18 | 2023-07-21 | AQM | 2023-07-21 | Servpro | SES report issued. Servpro deep-cleaned all impacted areas. Clearance test passed. Dehumidifier installed
2023-07-17 | Ray Bldg | ---- | Humidity Mold | Owned | Ground Level | 28 Tyson Dr | Augusta | Mold | Assess cause of mold growth on lower walls during renovation | 2023-07-20 | 2023-07-24 | NA | NA | Benchmark | Contractor (Benchmark) removed moldy sheetrock; SES advised on how to control humidity during renovation
2023-07-18 | OCME | DPS | Conference Room Ceiling Mold | Owned | OCME / Conference Rm (Ground Lvl) | 30 Hospital St | Augusta | Mold | Assess mold growth on ceiling tile in Conference Rm | 2023-07-25 | 7/28/23 (email) | NA | NA | NA | Ceiling tile removed prior to SES inspection. Details of plumbing leak sent to PMD
2023-07-24 | Winthrop Warehouse | MSL | Winthrop Warehouse Dust | Leased | Storage Area | 1705 Route 202 Suite #1 | Winthrop | IAQ | Assess employee complaint of dust and hazardous work environment | 2023-07-26 | 7/28/23 (email) | NA | NA | Octagon | SES determined that the situations is not "hazardous" and there is common dust accumulation. Recommended general cleaner
2023-07-25 | DHHS-Lewiston | DHHS | Stockroom Odor | Leased | Stockroom (1st Floor) | 200 Main St | Lewiston | Odor | Assess cause of odor | 2023-08-03 | 8/3/23 (email) | NA | NA | NA | Odor determined to be related to new flooring installed by Lessor. Agency advised to ventilate the area to dissipate odor over time
2023-07-26 | 35 Anthony Ave | DHHS | Atrium Ceiling Leak | Leased | Atrium | 35 Anthony Ave | Augusta | Mold | Assess extent of mold resulting from roof leak. | 2023-07-26 | 7/23/23 (email) | AQM | 8/2/23 (Lab Results | Servpro | Servpro remediated the impacted areas. Clearance test passed
2023-08-02 | CDS-Ellsworth | CDS | Mold Concerns | Leased | EIPM Office | 190 Bangor Rd | Ellsworth | Mold | Employees are concerned about possibly mold on a window sash; there are other non-mold complaints also | NA | NA | AQM | 9/17/23, 11/5/23 | Unknown | AQM Inspected and provided report to address mold. Lessor did not follow recommendations. Follow-up report found several deficiencies. Agency broke lease and relocated
2023-08-03 | 109 Capitol St | DHHS | IAQ | Leased | Commissioner's Finance | 109 Capitol St | Augusta | IAQ | Assess employee complaint of allergy reaction | 2023-08-11 | 2023-08-21 | NA | NA | NA | SES inspection identified some very dusty work surfaces including a fan previously located elsewhere (dust contained fiberglass). Advised removal of fan and cleaning of dust
2023-08-08 | Tyson | DOC | Room 324 Odor | Owned | Room 324 | 25 Tyson Dr | Augusta | Odor | Assess cause of odor | 2023-08-09 | 2023-08-17 | NA | NA | NA | SES inspection identified cluttered and dusty conditions and complete lack of ventilation (door is kept closed). Advised cleaning and adding vent to door
2023-08-08 | Hospital St Fire Station | NA | Tennis Courts HazMat | Owned | Tennis Courts | 40 Hospital St | Augusta | Asbestos, Lead | Assess tennis courts for lead and asbestos prior to demolition | 2023-08-11 | NA | AQM | 8/18/23 (Lab Results) | NA | No lead or asbestos found
2023-08-09 | GBSD Building-D | MECDHH | Mold / Water Damage | Owned | Ground Level and 1st Floor | Mackworth Island | Falmouth | Mold | Assess cause and extent of mold | 2023-08-16 | 2023-08-24 | NTC | 2023-07-26 | Unknown | SES inspection identified mold on furniture, some lower walls and remaining carpet. GBSD removed all carpet and furniture and is managing the remediation
2023-08-15 | MFS-Benton | MFS | Basement Mold | Owned | Entire Basement Level | 57 Bangor Rd | Benton | Mold | Assess water damage and mold in Basement | 2023-08-18 | 2023-08-25 | NA | NA | Servpro | SES inspection identified mold due to humidity and groundwater. Servpro to address in early 2024.
2023-08-16 | DEP-Portland | DEP | Carpet Mold | Leased | Multiple areas | 312 Canco Rd | Portland | Mold | Test carpet for mold growth on one area of suspicion | 2023-08-29 | 2023-09-08 | Sevee & Mahar | Unknown | Envirovantage | SES inspection found no mold in carpets but found wet lower walls and mold growth along perimeter walls. Report issued to Lessor who is using his IEP and remediation firm to address the issues
2023-08-23 | DHHS-Lewiston | DHHS | Roof Leak | Leased | Fraud / 2nd Floor | 198 Main St | Lewiston | Water damage | Identify wet materials and advise on drying | 2023-08-24 | NA | NA | NA | NA | SES identified several small areas of wet walls. DHHS Staff dried walls using fans (verified with moisture meter)
2023-08-28 | Nash | SOS | Musty Odor | Owned | Basement | 103 Sewall St | Augusta | Mold | SES inspection identified mold growth in basement due to humidity and groundwater | 9/5/23, 9/12/23 | 2023-09-28 | NA | NA |  | SES inspection identified mold due to excess humidity. Report issued with recommendations. Remediation on hold pending overhaul of entire building. Dehumidifiers in basement stopped odors.
2023-08-30 | CSOB | SOS | 6th Floor Roof Leaks | Owned | 6th Floor - Attorney General Area | 111 Sewall St | Augusta | Water Damage | Assess impact from water intrusion due to heavy rain | 2023-08-30 | 2023-08-30 | NA | NA | Servpro | Servpro removed some walls and dried materials and carpets. Removed (under containment) minor areas of mold on lower walls. Rebuilding awaiting fix for roof
2023-08-31 | Blaine House |  | Living Room Mold on Wall | Owned | Living Room wall facing the New England Garden | 192 State St | Augusta | Mold | Assess mold on wall | 2023-08-31 | 2023-09-01 | NA | NA | NA | Mold on wall determined to be superficial and formed from humidity emanating from wall and light fixture. Source determined to be basement. Advised placement of dehumidifiers in basement and controlling rainwater runoff
2023-09-05 | Tyson | DOC | Musty Odors | Owned | 3rd Floor | 25 Tyson Dr | Augusta | Mold | Assess source of musty odors and wet ceiling tiles | 2023-09-07 | 2023-09-08 | NA | NA | NA | SES identified several water leaks and points of condensation above ceiling tiles. Leaks were addressed and ceiling tiles replaced
2023-09-11 | State House | Legislature | Library Mold | Owned | Law Library | 210 State St | Augusta | Mold | Assess report of mold suspected on wall AC units located on perimeter wall | 2023-09-12 | 2023-09-12 | NA | NA | Servpro | SES identified mold growth in most of the AC units and on bookshelves in 1 corner of the room, all due to humidity. Servpro deep-cleaned to remove mold
2023-09-19 | 221 State St | HETL | Unknown Liquid | Owned | Basement Rm 106 and adjoining areas | 221 State St | Augusta | Chemical / Unknown | Assess dark liquid leaking from HVAC ducts | 2023-09-20 | 2023-09-21 | NA | NA | NA | SES inspection determined that liquid was due to condensation inside ducts and old dust impacted by acid vapor (giving the dark color). Advised HETL that cleaning with standard, minimal precautions (PPE) is acceptable
2023-10-11 | Building-A | DPS-Computer Crimes | Basement Office Expansion | Owned | Basement, 2 rooms next to Evidence Storage Room | 15 Oak Grove Rd | Vassalboro | Pro-active Inspection | Assess suitability of rooms for uses as offices | 2023-10-18 | 2023-11-02 | NA | NA |  | SES identified several mold and wall-damage issues and discovered substantial mold growth in the Evidence Storage. Intended office use was abandoned. Mold remediation awaiting decision on relocation of evidence storage
2023-10-16 | 353 Water St | IF&W | Carpet Mold | Leased | Office Area | 353 Water St | Augusta | Mold & Bacteria | Servpro requested advice for carpet impacted by water and with strong sour odor | NA | NA | NA | NA | Servpro | Remediation managed by Lessor; After several unsuccessful cleaning attempts, the carpet was replaced
2023-10-19 | Greenlaw | HETL | Neutralization Sump Gases | Owned | Sample Neutralization (Room 128) | 47 Independence Dr | Augusta | Odor / Chemical | Employees concerned about possible airborne exposure to gases / chemicals | 2023-10-20 | 2023-10-20 | NA | NA | NA | SES determined that odors are from (minor) general / non-specific volatile compounds emanated from a poorly sealed sump pit. Advised HETL to seal the cover or provide aggressive exhaust ventilation
2023-10-23 | DOC-Auburn | DOC | Ceiling Mold | Leased | 2nd Floor, 1 room | 5 Burns St | Auburn | Mold | Assess mold growth on ceiling | 2023-10-24 | 2023-10-30 | NA | NA | Service Master | SES inspection conducted; report with remediation scope provided to Lessor. Successful remediation by Service Master
2023-10-23 | Gardiner Annex | DPFR | IAQ Concern | Leased | 1 cubicle area | 76 Northern Ave | Gardiner | IAQ & Mold | Conduct testing to address employee concerns | 2023-10-30 | NA | AQM | 2023-11-06 | NA | Testing by AQM identified normal conditions; mold growth not present on items of concern to employee
2023-10-23 | Gardiner Annex | DPFR | BFI Examiner Roof Leak | Leased | BFI Examiner Area | 76 Northern Ave | Gardiner | Water Damage | Assess impact from ceiling leak | 2023-10-30 | NA | NA | NA | NA | Water impact was predominantly to a table, only a very small area of carpet was wet. Drying fan set up and dried over next several days
2023-10-30 | CDS-Portland | CDS | Mold & Water Damage | Leased | Unknown Area | 1011 Forest Ave | Portland | Water Damage / Mold | SES asked to assist Leased Space in guiding Lessor to the required remediation and documentation | NA | NA | NA | NA | NA | Project is ongoing and being directed by the Lessor. SES will assist Leased Space as needed.
2023-11-03 | Hospital St Fire Station | None | Abatement Oversight | Owned | Unknown Area | 40 Hospital St | Augusta | Asbestos | SES was asked by PDC to provide 3rd party assessment of abatement contractor's work | NA | NA | AQM | 2023-11-13 | Unknown | AQM identified several deficiencies in protocol and equipment. After several re-inspections, contractor was cleared to begin
2023-11-06 | Gardiner Annex | DPFR | Water Cooler Mold | Leased | OPOR | 76 Northern Ave | Gardiner | Mold | Assess areas where water coolers had been installed | 2023-11-09 | 2023-11-16 | NA | NA | Servpro | Signs of leakage found in 2 of 8 locations, 1 of which contained mold growth. Informed Lessor, who used Servpro to successfully remediate
2023-11-17 | BMV-Scarborough | BMV | Mold | Leased | All Areas | 200 Expedition Dr | Scarborough | Mold | Project re-opened by BMV. Assisted with 3rd-party mold inspection. Identified several areas with definitive issues. Demand for remediation will be sent to Lessor | 2023-12-06 | NA | AQM |  |  | SES in conjunction with AQM identified mold issues related to humidity and a ceiling leak. A report will be issued to Lessor requiring remediation.
2023-11-20 | Vital Records | DHHS | IAQ | Owned | All Areas | 220 Capitol St | Augusta | IAQ | Conduct IAQ sampling in response to employee inquiry of any recent testing | 2023-11-22 | 2023-12-01 | NA | NA | NA | SES testing found all IAQ parameters to be within normal ranges except for low humidity, which is common in winter
2023-11-21 | CSOB | BGS | Deputy Commissioner's Office IAQ | Owned | 4th Floor - Employee Office | 111 Sewall St | Augusta | IAQ | Assess office for anything that could affect health | 2023-11-21 | 2023-12-01 | NA | NA | BGS | Identified dusty conditions. Found disproportionate amount of mold and starch in dust. Relocating printers to address starch. Assessing HVAC system to address mold
2023-11-27 | 45 Commerce Dr | SESC | IAQ | Owned | Human Resources Office | 45 Commerce Dr | Augusta | IAQ | Assess employee work areas for anything that could affect health | 2023-11-30 | 2023-12-22 | NA | NA | NA | Found all IAQ parameters to be within normal ranges except for low humidity, which is common in winter. Work areas were very dusty. Dust contained normal components. Report issued to address cleaning and dust
2023-11-30 | 85 Leighton Rd | OIT | Rodent Issue | Leased | OIT Print Room | 85 Leighton Rd | Augusta | Rodent | OIT reported foul odors and dead rodents in Print Room. SES inspected and provided recommendations for cleaning | 2023-11-30 | 2023-12-01 | NA | NA | Service Master | Service Master cleaning conducted in timely manner to avoid shut-down of print operations
2023-12-04 | State House | Legislature | Radon Assessment | Owned | All Areas | State House Station | Augusta | Radon | Assess building for radon per State and Federal standards | 2023-12-11 | NA | Goodwin Environmental | 12/26/23, 2/16/24 | NA | Identified elevated radon in 1st Floor. Ventilators installed - levels dropped below limit. Engineering study ongoing.
2023-12-05 | CSOB | DAFS | Commissioner's Office IAQ | Owned | 3rd Floor, Office of 1 employee | 111 Sewall St | Augusta | IAQ | Assess office for anything that could affect health | 2023-12-15 | 2024-01-12 | NA | NA | Servpro | Found excess dust accumulation throughout. Deep-cleaning performed.
2023-12-06 | Hospital St Fire Station | BGS-PDC | TSI Pipe | Owned | Outdoors (underground) | 40 Hospital St | Augusta | Asbestos | Apply DEP regulations and provide 3rd-Party testing | NA | NA | AQM | 2023-12-12 | Unknown | Consultation with DEP indicated the issue was not a regulated item. Testing confirmed asbestos. Contractor is free to properly remove the pipe

## 2024
Date Initiated | Building | Agency | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date BGS Onsite | BGS Rpt Date | IEP Name | IEP Rpt Date | Remediator Name | Outcome
2024-01-26 | DOL-Bangor | DOL | Mold Complaint | Leased | EMDC | 45 Oak St | Bangor | Mold | Assess area of concern for water damage and mold | 2024-02-08 | 2024-02-20 | NA | NA | NA | SES inspection found no water damage or mold issues except water-stained carpet (Microscopic exam indicated no mold in carpet)
2024-02-05 | GBSD Bldgs D, G, connector G-K | MECDHH | Haz Mat | Owned | Bldgs D, G, connector G-K | Mackworth Island | Falmouth | Hazmat | Assess materials for LBP and ACBM prior to planned renovations | NA | NA | RPF Environmental Testing and Consultants | 2024-04-10 |  | Information provided to PDC, to be addressed per their project plans
2024-02-08 | DOL-Presque Isle | DOL | Allergy Reaction | Leased | BUC / Claims Area | 66 Spruce St | Presque Isle | Allergy | Assess and test area of concern for potential allergens, including mold | NA | NA | AQM | 2024-03-17 | Lessor | Testing revealed normal conditions / no risks in area of concerned employee; minor issues in Basement and HVAC cabinet addressed by Lessor.
2024-02-09 | Smith Bldg | MCPDS | Water Damage | Owned | 1st and 2nd Floor at Conference Rm | 187 State St | Augusta | Water Damage | Assess water damage for potential mold | 2024-02-14 | NA | AQM |  |  | SES inspection found water damage and AQM conducted mold assessment; mold growth was not present.
2024-02-13 | 10 Water St | Maine State Museum | Ceiling Mold | Owned | History Storage Room | 10 Water St | Hallowell | Mold | Assess ceiling for mold growth | 2024-02-16 | NA | NA | NA | Octagon | Minor mold growth found on ceiling close to perimeter wall, due to humidity and item stacking. Octagon assigned to clean.
2024-02-26 | BMV HQ | BMV | Musty Odor | Owned | Finance Office (2nd Floor) | 101 Hospital St | Augusta | Odor | Determine cause of transient musty odor reported by room occupant | 2024-02-28 | 3/15/24 (email) | NA | NA | NA | Cause is likely related to a VAV box. Employee was relocated.
2024-02-29 | 10 Water St | Law Library | Ceiling Mold | Owned | Ceiling along back wall | 10 Water St | Hallowell | Mold | Assess suspected mold on ceiling | 2024-03-01 | 3/4/24 (email) | NA | NA | NA | Minor discoloration in some areas, determined (via surface test) not to be mold
2024-03-04 | OMAG Caribou Office | OMAG | Roof leak | Leased | NA | 14 Access Highway | Caribou | Mold | Determine if water impact to ceiling insulation has resulted in mold growth | NA | NA | AQM | 2024-03-26 | NA | Mold growth was not present in the insulation
2024-03-04 | MCPDS Caribou Office | MCPDS | Lease Hazmat | Leased | NA | 14 Access Highway | Caribou | Hazmat | Conduct a Hazmat assessment in the areas to be occupied by the agency | NA | NA | AQM | 2024-03-31 |  | AQM identified several issues warranting cleaning and follow-up; 2nd inspection found all issues resolved with satisfactory test results.
2024-03-05 | Ballard Center | BMV | Lease Hazmat | Leased | NA | 35 Medical Center Parkway | Augusta | Hazmat | Conduct a Hazmat assessment in the areas to be occupied by the agency | NA | NA | Icon Env (Lessor Provided) | Undated (onsite 3/28/24) | NA | Mold and hazardous materials not present
2024-03-19 | 14 Access Hwy | DOC | Lease Hazmat | Leased | N/A | 14 Access Highway | Caribou | Hazmat | Conduct a Hazmat assessment in the areas to be occupied by the agency | N/A | N/A | AQM | 2024-03-31 | N/A | Follow up testing recommendations indicate previously ID'd issues were addressed
2024-03-21 | OMAG Portland Office | OMAG | Musty Odors | Leased | Lower Level / basement | 125 Presumpscot St | Portland | Mold | Assess carpets and wall impacted by groundwater intrusion | 2024-04-03 | 2024-04-26 | Northeast Test Consultants (Lessor) | 2024-06-28 | Lakeside Abatement | Lower walls and carpet removed as recommended in report
2024-03-21 | Harlow | Various | Roof Leaks | Owned | Sporadic areas in 4th Floor; Custodial Area 1st Floor | 18 Elkins Ln | Augusta | Water damage | Assess impact from ceiling leaks in 4th Floor | 2024-03-25 | 3/29/24 (email) | NA | NA | NA | Minor water stains in several areas, 1 of which suspected as mold; surface test negative for mold. PMD advised to repair once roof is fixed.
2024-03-29 | Blaine House | Governor | 1st Floor Painting | Owned | 1st Floor, all areas | 192 State St | Augusta | Lead based paint | Coordinate LBP assessment of walls and ceiling in 1st Floor, to be used by Contractor in planned re-painting | 2024-04-19 | NA | AQM | 2024-04-30 | Licensed painting contractor | Licensed painting contractor hired by Blaine House, performed surface prep as needed and painted surfaces as planned
2024-04-01 | Visitor Information Center | Maine Office of Tourism | Lease Hazmat | Leased | NA | 114 North St | Houlton | Hazmat | Conduct a Hazmat assessment in the areas to be occupied by the agency | NA | NA | AQM (Lessor Provided) | 2024-04-12 | NA | Mold and hazardous materials not present
2024-04-09 | CSOB | BGS | Radon Assessment | Owned | All areas | 111 Sewall St | Augusta | Radon | Assess the building for occupant radon exposure | NA | NA | Goodwin Environmental | 4/9/24 and 5/14/24 | NA | With averages of 2 tests, all areas passed except Office in Boiler Room. SES follow-up test with Office door open resulted in pass. Door has been removed
2024-04-17 | Nash | BGS | HazMat | Owned | All areas | 103 Sewall St | Augusta | Hazmat | Assess all areas for asbestos, lead-based paint, water damage / mold and any other hazardous materials | NA | NA | Haley Ward | 2024-05-16 | NA | All Hazardous materials documented, to be addressed if needed in future / planned renovations; no present health risks indicated.
2024-04-17 | Daschlager | BGS | HazMat | Owned | All areas | 55 Capitol St | Augusta | Hazmat | Assess all areas for asbestos, lead-based paint, water damage / mold and any other hazardous materials | NA | NA | Haley Ward | 2024-05-28 | NA | All Hazardous materials documented, to be addressed if needed in future / planned renovations; no present health risks indicated.
2024-04-17 | McLean | BGS | HazMat | Owned | All areas | 193 State St | Augusta | Hazmat | Assess all areas for asbestos, lead-based paint, water damage / mold and any other hazardous materials | NA | NA | Haley Ward | 2024-05-28 | NA | All Hazardous materials documented, to be addressed if needed in future / planned renovations; no present health risks indicated.
2024-04-29 | CSOB | BGS | Exhaust Duct Cleaning | Owned | Cross Café, 1st Floor | 111 Sewall St | Augusta | General Cleanliness | SES asked to assess location and access to exhaust ducts, due to need for cleaning | 6/5/24 and multiple through 8/30/24 | 4/29/24 (email) | NA | NA | NA | 9/19/2025 BGS Director will talk to Fire Marshall to understand regulations and requirements of the vent, cleaning, and suppression system.
2024-05-02 | 333 Cony Rd | DACF | HazMat | Owned | Entire Building | 333 Cony Rd | Augusta | Hazmat | Assess all areas for asbestos, lead-based paint, water damage / mold and any other hazardous materials | NA | NA | Haley Ward | 2024-05-02 |  | ACBM: Nine-inch by nine-inch (9x9) off-white floor tile with brown flecks and associated black adhesive • Mudded pipe fitting insulation • Exterior window glazing
2024-05-13 | 45 Commerce Dr | DPS | Health Complaint | Leased | Augusta Regional Communications Center (9-1-1 Center) | 45 Commerce Dr | Augusta | IAQ | Assess work area for any conditions that could lead to health issues. | 2024-06-05 | 2024-06-20 | NA | NA | NA | All IAQ parameters within guidelines. No mold or water damage. Dust composition typical, but excess accumulation on surfaces. Recommended to perform deep cleaning of dust.
2024-05-17 | CSOB | DECD | Ceiling Plumbing Leak | Owned | DECD / 3rd Floor | 111 Sewall St | Augusta | Mold | Assess mold from slow, chronic plumbing leak in ceiling | 2024-05-23 | 2024-05-23 | NA | NA | Servpro | Small area of ceiling and wall removed. Sheetrock replaced by PMD.
2024-05-21 | Gardiner Annex | NA | Ant Issue | Leased | Women's Restroom | 76 Northern Ave | Gardiner | Pest | Assess for any possible water damage related to ant issue | 2024-05-21 | 5/21/24 (email) | NA | NA | NA | No water damage or mold found. Lessor to address ant issue.
2024-05-22 | Cultural Bldg | NA | Humidity Mold | Owned | Various locations, basement and 1st Floor (unoccupied and undergoing construction) | 230 State St | Augusta | Mold | Assess surfaces for suspected mold growth | 2024-05-29 | NA | NA | NA | Atlantic Environmental | Minor humidity-related mold on some surfaces, to be addressed during construction and planned cleaning
2024-05-22 | Pine State Building Facility | NA | Odor | Leased | Court Records | 337 State St | Augusta | Odor | Assess unknown odor and suspected bird nesting in wall | 2024-05-23 | 5/23/24 (email) | NA | NA | NA | Odor (minor) due to dirty conditions along wall and possibly bird nest inside wall. Agency to work with Lessor to correct.
2024-06-03 | Quoddy Head State Park | DACF | Hazmat | Owned | Map Room, Lighthouse | 973 S. Lubec Rd | Lubec | Hazmat | Test materials, not previously tested, for asbestos and PCBs prior to renovations | NA | NA | AQM | 2024-06-12 | NA | No asbestos or PCBs identified. Report received 6/25/24
2024-06-11 | Central region HQ | DACF | Cracks in Flooring | Owned | Men's Bathroom | 87 Airport Rd | Old Town | Asbestos | Assess risk from cracks in ACBM floor tile that are planned to be covered with new flooring | NA | NA | NA | NA | NA | Based on detailed photos from Agency, the flooring is intact and well-adhered to the underlayment. There is no risk.
2024-06-13 | Bean Barn, Bolduc Correctional Facility | DOC | Roof Leaks and Mold | Owned | 1st Floor, all areas | 516 Cushing Rd | Warren | Mold | Assess building for damage and mold growth due to recurring roof leaks | 2024-06-18 | 2024-06-28 | NA | NA | NA | SES recommended all finish materials be removed in 1st Floor. DOC to return the building to "barn use" only and use general contractor for work.
2024-06-20 | Gardiner Annex | BOI | Roof Leak | Leased | File Room | 76 Northern Ave | Gardiner | Water Damage | Assess carpet for mold risk following roof leak | 2024-06-21 | 6/21/24 (Verbal) | NA | NA | NA | SES found carpet dry except under a file cabinet; moved file cabinet and advised to use fan to allow rapid drying of carpet
2024-06-20 | MFS Greenville Ranger Station | MFS | Building renovation | Owned | All areas | 43 Lakeview St | Greenville | Mold | Assess mold in crawlspace identified by Engineer during structural inspection | NA | NA | AQM | 2024-09-15 | NA | Mold Air samples OK in occupied areas. MFS awaiting decisions on building renovation or demolition.
2024-06-24 | Gardiner Annex | BFI | Roof Leak | Leased | Conference Rm | 76 Northern Ave | Gardiner | Water Damage | Assess carpet for mold risk following roof leak | 2024-06-24 | 6/24/24 (Verbal) | NA | NA | NA | SES found carpet dry except in 1 very small spot; advised to use fan to allow rapid drying of carpet
2024-06-24 | Blaine House | Governor | Heat Pump Leak | Owned | 2nd & 1st Floor | 192 State St | Augusta | Water Damage | Assess extent of water damage and mold potential | 2024-06-24 | 2024-06-27 | AQM | 2024-08-23 | Servpro | 1 small area of upper wall in 1st Floor Hallway not dried in timely manner. Servpro removed wall and cleaned. Air samples passed.
2024-06-24 | Blaine House | Governor | Dining Room Mold | Owned | Dining Room | 192 State St | Augusta | Mold | Assess blemishes on wallpaper (suspected to be mold) | 2024-06-28 | 7/2/2024 (email) | NA | NA | NA | Blemishes not mold (determined to be degradation in finish)
2024-06-25 | Deering | DACF | Employee Concern | Owned | Ceiling leaks 3rd and 1st Floor | 90 Blossom Ln | Augusta | Mold | Assess potential for mold in areas of minor water impact | 2024-06-26 | 6/26/24 (email) | NA | NA | NA | All areas of water impact were very minor with no indications of mold or potential for mold.
2024-07-01 | DHHS-Bangor | DHHS | HazMat | Leased | All areas | 326 Harlow St | Bangor | Hazmat | Assess HazMat report provided by Lessor | NA | NA | Haley Ward | 2024-06-17 | NA | Only very minor issues present, Lessor direct to follow recommendations in report
2024-07-01 | 23 Water St | MCPDS | HazMat | Leased | Suite 200 | 23 Water St | Bangor | Hazmat | Assess HazMat report provided by Lessor | NA | NA | Haley Ward | 2024-07-16 |  | Only very minor issues present, Lessor direct to follow recommendations in report
2024-07-02 | Deering | DOE | Musty Odor Jul2024 | Owned | 1st Floor next to Tunnel entrance: rooms 128 & 129 | 90 Blossom Ln | Augusta | Mold / Odor | Assess conditions in Tunnel that may contribute to reported odors | 2024-07-08 | 2024-08-27 | NA | 2024-09-08 |  | AQM conducted testing and made no recommendations based on results. AQM observed spaces well kept and dehumidified installed.
2024-07-05 | DDPC Building F | DOC | Asbestos | Owned | Evidence Room and Office | 102 Hogan Rd | Bangor | Asbestos | Assess conditions in ceiling tiles, mastic and floor tiles prior to renovations | NA | NA | AQM | 2024-07-16 | Atlantic Environmental Contractors | Asbestos materials removed per DEP regulations prior to renovations
2024-07-10 | DHHS Monmouth Crisis House | DHHS | Mold Jul2024 | Leased | DHHS | 27 Plossay Shores | Monmouth | Mold | Assess presence of mold in the home | NA | NA | AQM | 2024-07-21 | Servpro | Lessor provided remediation per recommendations in AQM's report.
2024-07-11 | DHHS-Lewiston | DHHS | HazMat | Leased | DHHS Leased Area only | 198 Main St | Lewiston | Hazmat | Assess HazMat report provided by Lessor | NA | NA | AQM | 2024-07-01 | Octagon | Minor mold issue identified. Lessor provided Octagon to remediate / clean.
2024-07-18 | Bolduc Correctional, Housing Unit #1 | DOC | Suspected Mold | Owned | Storage Room for cleaning chemicals | 516 Cushing Rd | Warren | Mold | Assess residue on floor for suspected mold | 2024-08-15 | 2024-08-26 | NA | NA | NA | Appearance not like mold; surface test found no mold - residue likely from cleaner spills
2024-07-19 | Manager's Residence & Todd's Point Bath House | DACF | Roof Renovation | Owned | Reid State Park | 375 Seguinland Rd | Georgetown | LBP | Advise on regulations applicable to removal and disposal of wood fascia with LBP | NA | NA | NA | NA | NA | Agency advised on protocol for disposal of materials with LBP
2024-07-29 | MCPDS-Lisbon | MCPDS | HazMat | Leased | MCPDS Leased Space | 64A Lisbon St | Lewiston | Hazmat | Assess HazMat report provided by Lessor | NA | NA | AQM | 2024-07-26 | Mattra | Mold issue identified and remediated per recommendations in AQM report. Clearance testing passed.
2024-08-06 | 19 Union St | OCP | Humidity/ Mold | Owned | 1st Floor | 19 Union St | Augusta | Mold | Assess reports of excess humidity, condensation affecting ceiling tiles, and (found 8/21) mold on several chairs | 8/22/2024, Deep Insp 9/16-18/2024 | 9/19/24 (email) | AQM | 2024-09-11 | Servpro | Humidity cause identified and corrected. Servpro removed small area of 1 wall and carpets in 3 rooms. All areas cleaned, clearance testing passed.
2024-08-06 | CSOB | HR | Toilet Overflow | Owned | Area by 4th Floor Women's Rest Room | 111 Sewall St | Augusta | Mold / Sanitation | Assess potential for sewage impact and dry materials to prevent mold growth. | 8/6/2024, multiple through Nov2024 | 2024-10-18 | NA | NA | Servpro | Determined that the source was clean water without toilet bowl contents. Testing found 1 small area under chair pad with mold. All impacted carpet was steam-cleaned.
2024-08-08 | 45 Commerce Dr | DPS | Excess Humidity | Leased | Augusta Regional Communications Center (9-1-1 Center) | 45 Commerce Dr | Augusta | Mold | Assess Lease for Lessor responsibility to control humidity | NA | 8/12/24 (email) | NA | NA | NA | Evaluation of lease found no Lessor responsibility for controlling humidity. Agency informed that they will be financially responsible.
2024-08-16 | Tyson | DOC | Humidity Mold | Owned | DOC Main Offices, 3rd Floor | 25 Tyson Dr | Augusta | Mold | Assess mold from excess humidity | 8/16/2024, 8/23/24 | NA | AQM | 2024-08-27 | Servpro | Diffusers replaced in offices, flex-duct replaced in offices and main area. Servpro deep-cleaned all areas.
2024-08-19 | GBSD Gym Annex | MECDHH | HazMat Assessment | Owned | Gym Annex | Mackworth Island | Mackworth Island | HazMat | Assess materials for LBP and ACBM prior to planned renovations | NA | NA | AQM | 2024-10-28 | NA | Information provided to PDC, to be addressed per their project plans
2024-08-21 | 19 Union St | OCP | Humidity Mold | Owned | 1st Floor | 19 Union St | Augusta | Mold | Assess mold from excess humidity and water damage in Rm 110 | 2024-08-22 | NA | AQM | 9/11/24, 10/2/24 | Servpro, PMD | Minor office items with mold discarded. Wall remediated in Rm 110. Carpet removed in Rm 103 & Custodial. PMD deep-cleaned all other areas
2024-08-21 | MFS Office | DACF | Flooring Renovation | Owned | Kitchen, Bath (2) and Closet | 87 Airport Rd | Old Town | Asbestos | Remove ACBM linoleum flooring | NA | NA | AQM | 2023-02-16 | Octagon | Flooring removed under containment; project completed.
2024-08-22 | CSOB | OMAG | Window Leak | Owned | 7th Floor, 1 office | 111 Sewall St | Augusta | Water Damage | Assess water impact to sheetrock surrounding window; advice asked by PMD | 2024-08-22 | NA | NA | NA | NA | Impact area with potential mold found to be very minor. PMD advised to make planned repairs and instructed on how to handle small pieces of material with mold. PMD made repairs and cleaned area.
2024-08-22 | Crime Lab | DPS | Ceiling Tile Mold | Owned | Upper level, several rooms with water impact to ceiling tiles | 26 Hospital St | Augusta | Mold | Assess potential mold on ceiling tiles | 2024-08-23 | 8/23/24 (email) | NA | NA | NA | Only 1 tile with small area of mold; other tiles had stains only. PMD advised to replace tiles and address causes.
2024-08-26 | BMV HQ | BMV | Ceiling and Window Leaks | Owned | 1 Office each on 2nd and 1st Floors | 101 Hospital St | Augusta | Water Damage / Mold | Assess potential mold from roof and window leaks | 2024-09-25 | 10/23/24 (email) | AQM | 2024-09-08 | Octagon | AQM tested and provided report. SES inspected and sent instruction to Octagon for remediation. Ongoing.
2024-08-27 | Butler Bldg, MFS | MFS | Exterior Painting | Owned | Exterior, All | 87 Airport Rd | Old Town | Lead based paint | MFS asked for guidance for planned re-painting of exterior | NA | 2024-08-30 | NA | NA | NA | SES advised MFS on regulations and protocols for renovation with LBP. Agency advised to seek renovation funding with BGS Management.
2024-08-28 | Center Bldg |  | Fireproofing | Owned | 1st Floor and Basement | 67 Independence Dr | Augusta | ACBM and LBP | Provide guidance to PDC and Architect on what materials require testing and abatement | 2024-12-17 | an | Haley Ward | 2025-01-08 |  | *pipe insulation and associated mud-insulated pipe fittings - basement main corridor - sprinkler service room - room adjacent to vault access - electrical room - room adjacent to southeast stairwell - southwest stairwell and adjoining room - northwest mechanical room *Exterior window caulking
2024-08-29 | Tyson | DOC | 3rd Floor Hall Water Damage | Owned | 3rd Floor DOC Hallway | 25 Tyson Dr | Augusta | Water Damage | Assess extent of water damage and mold potential | 2024-08-29 | 2024-11-18
2024-09-05 | DOL-Presque Isle | DOL | Employee Complaint | Leased | Vocational Rehab (VR) Area | 66 Spruce St | Presque Isle | IAQ | Assess area of concern to employee | NA | NA | AQM | 10/8/2024 (follow-up 1/7/2025) | Lessor | AQM identified several issues warranting cleaning and follow-up; 2nd inspection found all issues resolved with satisfactory test results.
2024-09-10 | 10 Water St |  | Upper Wall Mold | Owned | Record Center / concrete walls in corners | 10 Water St | Hallowell | Mold | Assess suspected mold on some concrete upper walls and in corners | 2024-09-16 | 9/18/24 (email) | NA | NA | PMD / Servpro | Small areas of "mildew" type mold on concrete from condensation. PMD cleaned most, and Servpro cleaned high areas near ceiling
2024-09-13 | Staff House, Blaine House | Governor | Demolition | Owned | All areas | NA | Augusta | Mold | Assess conditions prior to employees entering to remove items | 2024-09-26 | 2024-10-15 | NA | NA | NA | No structural safety issues found. Surface mold from humidity found throughout. Blaine Staff advised to wear N95 masks when inside.
2024-09-17 | DDPC Bldg H | NA | Mold exposure | owned | Room 115 | 106 Hogan Road | Bangor | Mold | Remove carpet and pad; Detail, clean, treat all areas of Rm 115 | NA | NA | AQM | 2024-09-20 |  | AQM identified several issues warranting cleaning and follow-up; 2nd inspection found all issues resolved with satisfactory test results.
2024-09-30 | BMV-Waterville | BMV | Lease Hazmat | Leased | Agency leased area only | 21 College Ave | Waterville | Hazmat | Assess HazMat report provided by Lessor | NA | NA |  |  |  | Lessor provided reports for limited hazmat assessment and air handler inspection; only recommendation was to implement plan for regular maintenance on air handler.
2024-10-01 | CDS-Brunswick | CDS | Lease Hazmat | Leased | Agency leased area only | 29 Burbank Ave | Brunswick | Hazmat | Assess hazmat report provided by Lessor | NA | NA | AQM | 2024-10-01 |  | AQM identified several issues warranting cleaning and follow-up; 2nd inspection found all issues resolved with satisfactory test results.
2024-10-02 | Ray Building | NA | Sewage Backup | Owned | 1st Floor & Basement | 28 Tyson Dr | Augusta | Sewage | Clean sewage, remove impacted materials, dry and sanitize | 2024-10-03 | NA | NA | NA | Servpro | Impacted materials removed and surfaces sanitized. E.coli swabs (from AQM) were all negative.
2024-10-11 | 19 Union St | OSA | Ceiling Leaks | Owned | OSA / 2nd Floor | 19 Union St | Augusta | Mold | Assess suspected mold in small area of carpet and on several ceiling tiles | 2024-10-15 | 2024-10-18 | NA | NA | NA | Ceiling tiles were only water-stained, and surface test revealed no mold growth in carpet
2024-10-16 | 5 Chimney Loop | PMD | Asbestos in Mortar | Owned | Boiler Room | 5 Chimney Loop | Augusta | Asbestos | A PMD employee expressed concern for contractors doing exterior work, grinding mortar without containment | NA | 10/16/24 (email) | Absolute Resource Assoc | 2023-06-19 | NA | Based on a recent testing report, the mortar does not contain asbestos; employee's supervisor informed
2024-10-23 | Greenlaw | DHHS / HETL | Chemical Odors | Owned | Rooms 453 and 306 | 47 Independence Dr | Augusta | Odor | Assess transient odors of concern | 2024-10-23 | 10/23/24 (verbal) | NA | NA | NA | Assessed conditions and mechanical systems, including operation of exterior generators. No odors or issues found. Advised Agency to contact SES immediately if issues reoccur
2024-10-24 | BMV-Springvale | BMV | Investigations Office Mold | Leased | Investigations Office | 456 Main St | Springvale | Mold | Assess suspected mold in one office | NA | NA | AQM | 2024-10-28 | NA | Mold from humidity and water damage to walls found in office. BMV advised not to use office until the planned full interior renovation of the building within the next several months
2024-10-31 | Cultural Bldg | NA | Ceiling Mold | Owned | Atrium / Ceiling | 230 State St | Augusta | Mold | SES asked for advice for planned mold remediation of several sections of ceiling | 2024-11-06 | 11/6/2024 (verbal) | NA | NA | Atlantic Environmental | Work completed as part of ongoing renovation project.
2024-11-01 | 218 Fairbanks Rd | CDS | Lease Hazmat | Leased | All areas | 218 Fairbanks Rd | Farmington | Hazmat | Assess HazMat report provided by Lessor | NA | NA | AQM | 2024-11-18 |  | Only very minor issues present, Lessor direct to follow recommendations in report
2024-11-01 | 130 Oak St | Public Defense Service | Lease Hazmat | leased | Siote 5 | 130 Oak St | Ellsworth | Hazmat | Assess HazMat report provided by Lessor | NA | NA | AQM | 2024-11-11 |  | Only very minor issue present, Lessor direct to follow recommendations in report. Not a significant risk for radon.
2024-11-04 | 3 Chimney Loop | DEP | Potential Asbestos | Owned | 2nd Floor Storage | 3 Chimney Loop | Augusta | Asbestos | ceiling debris | 2024-11-04 | n/A | AQM | 2024-11-12 | N/A | Ceiling debris non-detect for asbestos.
2024-11-13 | BMV-Augusta | BMV | Printer Concern | Owned | Data Management / 2nd Floor Printer Area | 101 Hospital St | Augusta | IAQ | Assess employee concerns for transient / sporadic coughing | 2024-11-13 | 2024-11-21 | NA | NA | NA | BGS SES visited site; recommended to cease use of fan directed towards printers and increase frequency of surface cleaning in printer area and employee workstations.
2024-11-18 | Dover Foxcroft PD | DOC | HazMat/ IAQ | Leased | Parole/Probation Office | 182 E Main St | Dover-Foxcroft | HazMat | Conduct HazMat and IAQ assessment due to soft flooring and odor concerns | 2024-10-30 | NA | AQM | 2024-12-03 |  | BGS and DOC terminated the lease and relocated staff from the space immediately after receiving AQM's report.
2024-11-19 | Smith-Merrill | Public Defense Service | Ceiling Tile Mold | Owned | Rm 102 | 187 State St | Augusta | Mold | Office ceiling tiles have water stains on them. DOL requested tiles be inspected for mold. | 2024-11-20 |  | NA | NA |  | BGS SES verified and inspected for mold; no current concerns; submitted work order for replacement tiles.
2024-11-22 | CSOB | OMAG | Ceiling Tile Mold | Owned | 5th Floor, AG Area, Harvey Workstation | 111 Sewall St | Augusta | Mold | Workers IVO C. Harvey's cube stated the tiles around diffuser were dirty and needed to be cleaned/replaced | 2024-11-22 | NA | NA | NA | NA | Workorder requested from PMD to replace ceiling tiles in DOE (Partridge) and AG (Harvey).
2024-11-25 | Ellsworth Barracks | DPS | Building IAQ / Odors | Leased | All Areas, 1st Floor | 180 Bangor Rd | Ellsworth | Odor | Assess odors in the building | 2025-01-23 |  |  |  |  | BGS SES visited site; no odors detected at the time. Surface samples taken; awaiting results.
2024-11-26 | 45 Commerce Dr | DAFS | IAQ | Leased | Security and Employment Service Center | 45 Commerce Dr | Augusta | IAQ | Assess employee concerns for coughing and headaches | 12/4/2024 & 1/8/2025 | 1/16/25, Rev 1/25/25 | NA | NA | Servpro | SES verified and identified mold issue. SES and Leased Space divisions are working with the landlord to address the HVAC operation and mold issues.
2024-12-04 | Town of Mexico | DOC | Full Hazmat | leased | Probation and Parole - 2 offices w/ access to break room and bathroom | 134 Main St | Mexico | Hazmat | New lease hazmat | NA | NA | AQM | 2024-12-09 |  | Asbestos - finished systems appeared in good condition, floor tiles do not appear to be damaged to the point of an exposure risk. Due to age of bldg (1952), ACBM is present. Lead paint could also be present due to age of construction. Painted surfaces appeared in good condition therefore not tested. AQM recommended to replace water stained ceiling tiles to prevent perceived notion that mold growth is present.
2024-12-23 | Greenlaw | DHHS | Exhaust Odor | owned | Rooms 403, 407, 417 | 47 Independence Dr | Augusta | Odor | Assess odors in those specific rooms | 2024-12-23 |  | NA | NA | NA | Assessed conditions and mechanical systems. No odors found. Advised Agency to contact SES immediately if issues reoccur. Building control on scene to assess issues with supply air ventilation.

## 2025
Date Initiated | Building | Agency | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date BGS Onsite | BGS Rpt Date | IEP Name | IEP Rpt Date | Remediator Name | Outcome
2025-01-08 | 2 Anthony Dr | DHHS | IAQ | Leased | OCFS 1st floor - Intake | 2 Anthony Dr | Augusta | IAQ/Dust/ Mold | Assess employee concerns for allergies | 2025-01-13 | 1/17/2025 (email) | NA | NA | NA | Dust issue in the area, no mold. Emailed DHHS with recommendation for a thorough dust cleaning and (possibly) ventilation improvements.
2025-01-02 | Deering | DOE | Moldy Odors | Owned | Tunnels in vicinity of Electrical Rooms | 90 Blossom Way | Augusta | Mold/Odors | Assess employee concerns for moldy odors | 2025-01-17 | 1/27/25 (email) | NA | NA | ServPro | Mold remediation complete. PMD to upgrade electrical to allow for ERV ventilator operation and to install several dehumidifiers.
2025-01-30 | Elkins | LRB | Mold/Asbestos | Owned | Suite 204 | 19 Elkins Ln | Augusta | Mold/Asbestos | Test tiles/mastic for asbestos, test cabinets/bench for lead | 2025-01-31 | NA | AQM | 2025-02-24 | Octagon Restoration | Tiles and mastic tested positive for asbestos. Built-in cabinet tested positive for lead based paint. Rooms 204A and 204B to be abated
2025-02-03 | 19 Union ST | BABLO | Employee IAQ Complaint | Owned | 3rd Floor | 19 Union St | Augusta | IAQ | Assess one employee complaints of allergy-like and breathing symptoms | 2025-02-10 | 2025-02-20 | NA | NA | BABLO | Cause likely related to excess dust accumulation and air-supply vents intentionally blocked by employees. SES recommended deep-cleaning of dust and unblocking all air supply vents.
2025-02-07 | Harlow Building | Multiple | dirty air vents | Owned | all floors | 18 Elkins Ln | Augusta | IAQ/ Dust | Assess employee concerns for IAQ and dust on air vents | 2025-02-14 | 2/24/2025 (email) | NA | NA | PMD | Issue is dust only, mostly on air returns. PMD will clean all of the air vents throughout Harlow.
2025-02-10 | 3 Chimney Loop | DEP | Ceiling Mold | Owned | DEP-Response Training Room | 3 Chimney Loop | Augusta | Mold | Determine cause of mold; provide remedial recommendations | 2025-02-12 | 3/7/25 (email) | NA | NA | PMD | PMD cleaned and re-painted ceiling; will make changes to control humidity
2025-02-10 | 7 Chimney Loop | DEP | Carpet Mold | Owned | DEP-Response Main Offices | 7 Chimney Loop | Augusta | Mold | Assess water impact to carpets and suspected mold growth | 2025-02-12 | 2/25/2025 (email) | NA | NA | NA | Mold growth not present in carpets; carpets appeared dirty; advised PMD to deep-clean carpets
2025-02-18 | 21 College Ave, Waterville | BMV | Air handler inspection | leased | BMV - license | 21 College Ave | Waterville | IAQ | Inspection of air handler #5 | NA | NA | AQM | 2025-02-22 | NA | None warranted based on observations and sample results other than ensuring cleanliness of Air Handler #5 through routine maintenance and cleaning as well as filter changes.
2025-02-19 | 10 Water St | Archives | Rodent Feces | Owned | Records Center | 10 Water St | Augusta | Rodent | Assess buildup of rodent feces next to and under shelves along 1 or more walls | 2025-02-26 | 2/27/2025 (email) | NA | NA | PMD | Residue on floors determined to be construction debris related to past roof work. PMD will have custodians clean.
2025-03-05 | 15 York St | DOC | IAQ/Mold | Leased | Probation/Parole Office | 15 York St | Biddeford | IAQ/Mold | Assess employee concerns for IAQ and mold in offices | 2025-03-20 | NA | AQM | 2025-04-17 | Octagon Restoration | BGS and DOC terminated the lease and relocated staff from the space.
2025-03-06 | Bangor District Court | Judicial Branch | Asbestos Debris | Leased | Unknown | 78 Exchange St | Bangor | Asbestos | Assist DEP with critical issue from uncontrolled demolition | NA | NA | NA | NA | Unknown | SES worked with DEP until it was determined that the issue was at the Penobscot County Courthouse. DEP continued the issue with County Staff
2025-03-10 | 150 Main St |  | Leased Space HazMat | Leased | All leased areas | 150 East Ave | Lewiston | HazMat | Conduct HazMat assessment for lease renewal | an | an | AQM | 2024-03-10 | NA | Small area of mold remediated by cutting out sheetrock and replace with clean piece.
2025-03-14 | Maine State Library - Warehouse | Library | Debris | Owned | Storage area for Library Cartridges | 1705 Rt 202, Winthrop, Me | Winthrop | Asbestos / Mold | Assess residue on talking boxes/cartridges for asbestos and mold | 2025-04-01 | 4/3/2025 (email) | AQM | 2025-04-11 | NA | SES determined residue is not mold; AQM determined no asbestos content. Material is likely dirt / mud from construction. Items may be safely cleaned or disposed.
2025-03-16 | BMV Office/ Mobile RV | BMV | Leased Space HazMat | Leased | BMV Mobile Vehicle | 17 Stackpole Dr | Machias | HazMat | Conduct HazMat assessment for lease of small office space to be used with Trailer type (mobile) vehicle | NA | NA | Haley Ward | 2025-04-17 | NA | No issues found. Testing not conducted, materials that may include asbestos all in good condition. Suspect asbestos materials listed for future reference if become deteriorated or renovated.
2025-03-17 | BMV-HQ, Augusta | BMV | Air-Return Dust | Owned | 2nd Floor | 101 Hospital St | Augusta | Dust/IAQ | Assess air-supply diffusers as Employees expressed concern for possible mold | 2025-03-18 | 3/25/25 (email) | NA | NA | PMD | Determined to be excess dust build-up on air-return grilles. PMD asked to clean.
2025-03-19 | CSOB | DAFS | Deputy Commissioner's Office | Owned | BGS Deputy Commissioner's Office, 4th Floor | 111 Sewall St | Augusta | Mold | Replace air-supply flex-duct and deep clean the office | 2025-03-19 | 3/21/25 (email) | NA | NA | Servpro | Work completed 3/26/25
2025-03-20 | 76 Northern Ave | DPFR | Mold/Odor | Leased | P. Valllaincourt + 2 offices | 76 Northern Ave | Gardiner | Mold/ Odor | Assess employee concerns for IAQ and potential mold in carpets | 3/24/2025, multiple visits thereafter | Multiple email reports from 3/25/25 through 5/16/25 | AQM | 2025-04-04 | ServPro | Carpets removed in ASD and Front Office; Asbestos floor tiles under carpet abated in ASD corridor. Carpets under floormats steam-cleaned in all areas where slab foundation is present.
2025-03-20 | 286 Water St | CDC | Dust/IAQ | Leased | entire leased area - 9th floor | 286 Water St | Augusta | Dust/ IAQ | Assess employee concerns for IAQ and dust on surfaces | 2025-03-31 | NA | AQM | 2025-04-19 | Unknown | Elevated particulates in 1 area, and visible surface dust in others. DHHS advised to have the areas deep-cleaned
2025-03-26 | Bangor District Court | Judicial Branch | Mold Cleaning | Leased | Unknown / Stored document boxes | 78 Exchange St | Bangor | Mold | Advise cleaning of documents and lab results | NA | NA | Evergreen Environmental, AQM | not dated / Unknown | Servpro | Judicial Branch requested advice on cleaning and lab results. SES determined that Evergreen's testing was not done per industry standard, biasing results. Servpro re-cleaned and docs retested by AQM; no mold remaining.
2025-04-08 | 286 Water St | DHHS | IAQ | leased | 3rd floor (Health Inspection Program) | 286 Water St | Augusta | IAQ | Assess employee concerns for IAQ | 2025-04-14 | NA | AQM | 2025-04-23 | NA | per AQM report: No mold or IAQ related recommendations warranted based on data collected. Determine source of fibrous particulate in the Office area and make necessary improvements / repairs.
2025-04-22 | State House/Capital Building | NA | leaking pipe/mold | owned | Elevator room |  | Augusta | Mold | repair leaky pipe/remediate mold | 2025-04-23 | NA | NA | NA | Servpro | Small amount of mold isolated to elevator pump room; Ongoing, to be remediated mid to late June
2025-04-28 | 286 Water St | DHHS | IAQ | leased | 3rd Floor (Health Inspection Program) | 286 Water St | Augusta | IAQ | Follow-up AQM's report for 4/8/25 project; collect dust, assess dust and fibers | 2025-04-28 | 5/8/25 (email) | NA | NA | NA | All dust samples indicate normal dust; fibers are common textile & cellulosic. Recommended better cleaning to prevent dust accumulation
2025-05-07 | CSOB | NA | Bird Carcasses | Owned | Basement, Concrete air-return tunnel at HVAC-2 | 111 Sewall St | Augusta | Pest | Several small bird carcasses discovered during inspection for other purposes | 2025-05-07 | NA | NA | NA | PMD | PMD workorder made on 5/9/25 to have Modern Pest remove the carcasses.
2025-05-27 | Bradbury State Park, Park HQ & Residence | DACF | HazMat | Owned | Living Areas and HQ Office | 528 Hallowell Road | Pownal | HazMat | Assess living areas of HQ / Residence for hazardous materials and mold | NA | NA | AQM, Goodwin | 7/29/2025, 7/17/25 |  | 9/23/2025 Discussions ongoing
2025-05-29 | 130 Oak St, Ellsworth | Public Defenders | HazMat | Leased | Suite 8, 2nd Floor | 130 Oak St | Ellsworth | HazMat | Hazardous Materials Assessment for new lease | NA | NA | AQM | 2025-06-03 | NA | No recommendations warranted; no issues or risks identified. Suspected ACBM materials should be tested prior to any future renovations.
2025-06-23 | Capital Judicial Center | Judicial Branch | Heat Issues | Leased | Multiple Areas | 1 Court St, Suite 201 | Augusta | Heat / Comfort | Advise employee on elevated heat issue | NA | 6/24/25 (email) | NA | NA | NA | SES advised employee on ASHRAE Standard 55 and the thermal comfort zone, and advised to contact SES through their Agency management for any further assistance
2025-06-23 | Lincoln District Court | Judicial Branch | Mold | Leased | Basement and Clerk's Office | 52 Main St | Lincoln | Mold | Advise Judicial Branch on mold and needed remediation in the Basement | NA | NA | AQM | 2025-04-23 |  | Ongoing
2025-06-23 | Bangor District Court | Judicial Branch | Mold on Documents | Leased | Documents stored in Mechanical / Boiler Room | 78 Exchange St | Bangor | Mold | Assess suspect contamination on documents transferred from Lincoln District Court | 2025-07-02 | 7/3/25 (email) | NA | NA | NA | Via microscopy, black substance on file flders determined not to be mold.
2025-06-25 | Songo Beach Concession Stand | DACF | Tree Damage | Owned | Sebago Lake State Park | 11 Park Access Road | Casco | Asbestos | Assess damage to roof and ceiling from fallen tree | NA | NA | AQM | 2025-07-03 |  | Ceiling panels determined to be Transite (asbestos-containing).
2025-06-27 | State House/Capital Building | NA | Security Renovation | Owned | Café 1st Floor | 210 State St | Augusta | Lead, Asbestos | Assess materials in Café prior to construction work | NA | NA | AQM | 2025-07-03 | Benchmark | No asbestos present; paint is lead-based. Surfaces repainted per RRP rules.
2025-06-30 | 41 Anthony Ave | DHHS | Water Damage | Leased | 1st and 2nd Floor, various areas | 41 Anthony Ave | Augusta | Water Damage | Dry impacted areas from broken refrigerator water-supply line on 2nd Floor | 2025-07-01 | NA |  |  | Servpro | Landlord hired ServPro to remove water-damaged materials and then Landlord completed reconstruction work after successful post-remediation testing completed by AQM.
2025-07-08 | 45 Memorial Circle | Maine Ethics Commission | HazMat | Leased | Suites 201 and 203 | 45 Memorial Circle | Augusta | HazMat | Hazardous Materials Assessment for new lease | NA | NA | AQM | 2025-07-06 | NA | No Issues or Hazardous-material issues found. Minor dust cleaning (air-supply diffusers) advised, to be completed by Custodial Staff.
2025-07-10 | Greenlaw | HETL | MTBE Odor | Owned | Organics, Extraction Lab | 47 Independence Dr | Augusta | Odor / Chemical | Assess odor migrating into work areas when extractions performed in hood | 2025-07-18 | 2025-09-05 | NA | NA | NA | Odors likely from MTBE during tube shaking outside of hood and other handling tasks, due to room changing to positive air-pressure under some situations
2025-07-15 | Cultural Building | Archives | Fireproofing Debris | Owned | Archives 1st Floor | 230 State St | Augusta | Asbestos | Assess fireproofing debris found on several shelves (asbestos test) | 2025-07-16 | NA | AQM | NA | Envirovantage & Servpro | Only 1 small piece of debris determined to contain asbestos, occurrence due to breach of containment at 1 area where plastic sheet attached to wall during remediation years ago. All Archive areas thoroughly cleaned, pro-active measure
2025-07-16 | 10 Water ST | MHPC | Water leak/ Mold | owned |  | 10 water St | Augusta | Water leak/ Mold | Water leak heat pump line/mold | 2025-07-16 | 2025-07-24 | AQM | 2025-08-12 | Servpro | Asbestos wall materials not present; Servpro removed wall and cleaned surfaces; PMD rebuilt wall
2025-07-22 | DHHS - Bangor | DHHS | IAQ | Leased | Div. of Support Enforcement and Recovery | 15 Maine St | Bangor | IAQ | Assess IAQ | 2025-07-31 | 2025-08-13 | NA | NA | Unknowm | No major issues found. To err on side of most caution, Recommended carpet steam-clean due to past history of elevated humidity
2025-07-22 | 6 Water St, Houlton | DOC | HazMat | Leased | DOC | 6 Water St | Houlton | HazMat | Hazardous Materials Assessment for new lease | NA | NA |  |  |  | No hazardous material issues found. Detail clean recommended, seal filter area of AC unit and remove items stored in Basement area.
2025-07-22 | BMV-Kennebunk | BMV | HazMat | Leased | NA | 63 Portland Rd | Kennebunk | HazMat | Hazardous Materials Assessment for new lease | NA | NA | AQM | 2025-07-21 |  | Full duct cleaning recommended
2025-07-28 | MCPDS-Portland | MCPDS | HazMat | Leased | All leased areas | 45 Exchange St | Portland | HazMat | Hazardous Materials Assessment for new lease | NA | NA | Haley Ward | 2025-09-09 | NA | Conditions reported as safe; report accepted after revision to provide additional info.
2025-07-29 | 64 Lisbon St | MECDHH | HazMat | Leased |  | 64 Lisbon St | Lewiston | HazMat | Hazardous Materials Assessment for new lease | NA | NA | AQM | 2025-07-26 |  | Inspected accessible areas in good condition. Inspected supply air diffusers; no mold growth or significant dust accumulation found.
2025-07-30 | Tyson | DEP | Vent Cleaning | Owned | DEP 1st Floor |  | Augusta | Mold | Assess mold growth on air-supply diffusers and need for cleaning | 2025-08-01 | 8/12/25 (email) | NA | NA | Servpro | Servpro cleaned diffusers and associated ducts, as needed
2025-08-05 | DHHS Hallowell | DHHS | Particulates | Leased | Riverview Outpatient Services | 47 Water St | Hallowell | IAQ | Assess airborne particulate levels following construction | 2025-08-08 | NA | AQM | 2025-08-18 | NA | Airborne particulates withing normal range
2025-08-14 | MCPDS Lewiston | MCPDS | Humidity / Mold | Leased | All leased areas | 64A Lisbon St | Lewiston | IAQ / Mold | Assess reports of excess humidity and suspected mold | 2025-08-19 | 2025-08-21 | NA | NA | NA | Mold not present. Assessed HVAC systems and provided guidelines that Lessor must follow to control humidity
2025-08-26 | BMV HQ | BMV | Suspected CO | Owned | 1st Floor Vehicle Services | 101 Hospital St | Augusta | IAQ | Baseline IAQ readings following incident of suspected CO exposure | 2025-08-28 | NA |  |  |  | Airborne particulates withing normal range
2025-09-08 | Presque-Isle District Courthouse | Judicial | Sewer Odor | Owned | All Areas | 27 Riverside Dr | Presque-Isle | Odor | Assess risk from issue resulting in sewage odors. All investigative and remedial work overseen by Judicial Branch; SES role was advisory | NA | 9/22/25 (email) | Allen’s Environmental Services, Inc. | Unknown | McGlinn’s Plumbing & Heating | Issues determined to be caused by multiple, partial blockages in the sewer line, resulting in sewage help-up within the plumbing. This resulted in microbial activity and odors, which permeated through drains and vent pipes. At no time did liquid sewage back-up out of the plumbing to impact building materials. Based on this, there was and is no environmental health risk.