## GivenAssume
Androscoggin Power Boilers #1 or #2
Given/Assumptions
New or Retrofit? | Retrofit | OAQPS Control Cost Manual
Extra retrofit cost factor | 1 | estimated
Generation capacity (MW) | 68 | estimated
SCR bypass included? | No | OAQPS Control Cost Manual
Fuel High Heating Value (Btu/gal) | 150000 | company report
Maximum Fuel Consumption Rate (gal/hr) | 4533.3333 | calculated | 680 | mmBtu/hr from company report
Maximum Annual Fuel Consumption (gal) | 39712000 | calculated
Maximum Annual Heat Input (mmBtu) | 5956800 | calculated
Number of SCR Operating Days | 365 | assumed
Uncontrolled NOx Concentration (lb/mmBtu) | 0.41 | company report
Uncontrolled NOx Emissions (tpy) | 383.1 | company report
Actual annual heat input (mmBtu) | 1868780.4878 | calculated
Required Controlled NOx Concentration (lb/mmBtu) | 0.041 | calculated from company estimate
Acceptable Ammonia Slip (ppm) | 2 | OAQPS Control Cost Manual
Fuel Volume Flow Rate (dscf/mmBtu) | 9190 | AP-42 | 6249200
Fuel Sulfur Content | 0.7% | company report
Number of SCR reactor chambers | 1 | OAQPS Control Cost Manual
ASR | 1.05 | OAQPS Control Cost Manual
Stored Ammonia Concentration | 29% | OAQPS Control Cost Manual
Reagent Molecular Weight (g/mole) | 17.03 | OAQPS Control Cost Manual
Reagent Density (lb/ft3 @ 60F) | 56 | OAQPS Control Cost Manual
Reagent Specific Volume (gal/ft3) | 7.481 | OAQPS Control Cost Manual
NOx Molecular Weight (g/mole) | 46.01 | OAQPS Control Cost Manual
Number of Days of Storage for Ammonia | 14 | OAQPS Control Cost Manual
Pressure Drop for SCR Ductwork H2O") | 3 | OAQPS Control Cost Manual
Pressure Drop for each Catalyst Layer (H2O") | 1 | OAQPS Control Cost Manual
Temperature at SCR Inlet (degrees F) | 650 | OAQPS Control Cost Manual
Equipment Life (years) | 20 | OAQPS Control Cost Manual
Annual Interest Rate | 7% | OAQPS Control Cost Manual
Inflation Since 1998 | 1.35 | CEPCI 2007/CEPCI 1998
Catalyst Cost, Initial ($/ft3) | 85.0158 | calculated | 3000 | /m3 from PacifiCorp report
Catalyst Cost, Replacement ($/ft3) | 85.0158 | calculated | 3000 | /m3 from PacifiCorp report
Electrical Power Cost ($/kWh) | 0.08 | company report
29% Ammonia Solution Cost ($/lb) | 0.058 | calculated | 400 | /ton from PacifiCorp report
Operating Life of Catalyst (hours) | 24000 | OAQPS Control Cost Manual

## Boiler Calcs
Boiler Calculations
2.3 QB = HVm-dotfuel
QB = | 150000 | Btu/gal * | 4533.3333 | gal/hr
QB = | 680 | mmBtu/hr
2.7 | CFPlant = actual mfuel/maximum mfuel
CFPlant = | 1868780.4878 | mmBtu/yr / | 5956800 | mmBtu/yr
CFPlant = | 31.37%
2.8 | CFSCR = tSCR/365 days
CFSCR = | 365 | days/ | 365 | days
CFSCR = | 100%
CFTotal = CFPlant x CFSCR
CFTotal = | 31.37% | * | 100%
CFTotal = | 31.37%
2.12 | qfluegas = qfuelQB(460+T)/(460+700oF)nSCR
qfluegas = | 9190 | ft3/min/(mmBtu/hr)* | 680 | mmBtu/hr*( | 460 | + | 650 | )/( | 460 | + | 700 | )/ | 1
qfluegas = | 5979837.931 | acfm
2.9 | ηNOx = (NOxin – NOxout) / NOxin
ηNOx = | ( | 0.41 | lb/mmBtu - | 0.041 | lb/mmBtu)/ | 0.41 | lb/mmBtu
ηNOx = | 90%
Uncontrolled NOx emissions (tpy) |  |  | 383.1

## SCR Reactor
SCR Reactor Calculations
2.19 | Volcatalyst = 2.81 x QB x ηadj x Slipadj x NOxadj x Sadj x Tadj/NSCR
Volcatalyst = | 2.81 | * | 680 | = | 1910.8
| 2.2 | ηadj = 0.2869 + (1.058 x η)
| ηadj = | 0.2869 | +( | 1.058 | * | 0.9 | )
| ηadj = | 1.2391
| 2.22 | Slipadj = 1.2835 – (0.0567 x Slip)
| Slipadj = | 1.2835 | - ( | 0.0567 | * | 2 | )
| Slipadj = | 1.1701
| 2.21 | NOxadj = 0.8524 + (0.3208 x NOxin)
| NOxadj = | 0.8524 | + ( | 0.3208 | * | 0.41 | )
| NOxadj = | 0.98393
| 2.23 | Sadj = 0.9636 + (0.0455 x S)
| Sadj = | 0.9636 | + ( | 0.0455 | * | 0.7 | )
| Sadj = | 0.99545
| 2.24 | Tadj = 15.16 – (0.03937 x T) + (2.74 x 10-5 x T2)
| Tadj = | 15.16 | - ( | 0.03937 | * | 650 | ) + | 2.74e-05 | * | 422500
| Tadj = | 1.146
Volcatalyst = | 3109.6532 | ft3 each = | 88.1232 | m3 each
2.25 | Acatalyst = qfluegas/(16 ft/sec x 60 sec/min)
| Acatalyst = | 5979837.931 | /( | 16 | * | 60 | )
| Acatalyst = | 6228.9978 | ft2
2.26 | ASCR = 1.15 x Acatalyst
| ASCR = | 1.15 | * | 6228.9978
| ASCR = | 7163.3475 | ft2
2.27 | l = w = ASCR1/2
| l = w = | 84.6366 | ft
2.28 | nlayer = Volcatalyst/(h’layer x Acatalyst)
| nlayer = | 3109.6532 | /( | 3.1 | * | 6228.9978 | )
| nlayer (calc) = | 0.16104
| nlayer = | 2
2.29 | hlayer = [Volcatalyst/(nlayer x Acatalyst)] + 1
| hlayer = | 3109.6532 | /( | 2 | * | 6228.9978 | ) + | 1
| hlayer = | 1.2496
2.3 | ntotal = nlayer + nempty
| ntotal = | 2 | + | 1
| ntotal = | 3
2.31 | hSCR = ntotal(c1 + hlayer) + c2
| hSCR = | 3 | * ( | 7 | + | 1.2496 | ) + | 9
| hSCR = | 33.7488 | ft

## Reagent
Reagent Calculations
2.32 | m-dotreagent = NOxinQBASRηNOxMreagent/MNOx
| m-dotreagent = | 0.41 | * | 680 | * | 1.05 | * | 90% | * | 17.03 | / | 46.01
| m-dotreagent = | 97.5185 | lb/hr
2.33 | m-dotsol = m-dotreagent/Csol
| m-dotsol = | 97.5185 | / | 0.29
| m-dotsol = | 336.2707 | lb/hr
2.34 | qsol = (m-dotvol/ρsol)Vsol
| qsol = | 336.2707 | * | 7.481 | / | 56
| qsol = | 44.9222 | gph
2.35 | Tank Volume = qsolt
| Tank Volume = | 44.9222 | * | 14 | * | 24
| Tank Volume = | 15093.8455 | gal

## DCC
Direct Capital Cost
2.36 | DC = QB[($3380/MMBtu/hr) + f(hSCR) +f(NH3rate) + f(new) + f(bypass)](3500/QB)0.35 + f(Volcatalyst)
| DC = | 680 | (( | 3380 | +
|  | 2.37 | f(hSCR) = {[$612/(ft-mmBtu/hr)]hSCR} - $187.9/(mmBtu/hr)
|  | f(hSCR) = | 6.12 | * | 33.7488 | - | 187.9
|  | f(hSCR) = | 18.6429 | /mmBtu/hr
|  | 2.38 | f(NH3rate) = [($411/lb/hr)(m-dotreagent/QB)] - $47.3/(mmBtu/hr)
|  | f(NH3rate) = | 411 | * | 97.5185 | / | 680 | - | 47.3
|  | f(NH3rate) = | 11.6413 | /mmBtu/hr
|  | 2.39 | f(new) = $0/(mmBtu/hr) for retrofit
|  | f(new) = | 0
|  | 2.41 | f(bypass) = $0/(mmBtu/hr) for no bypass
|  | f(bypass) = | 0 | /mmBtu/hr
|  | 2.43 | f(Volcatalyst) = VolcatalystCCinitial
|  | f(Volcatalyst) = | 3109.6532 | * | 85.0158
|  | f(Volcatalyst) = | 264369.7015
| DC = | 680 | * ( | 3380 | + | 18.6429 | + | 11.6413 | + | 0 | + | 0 | )*( | 3500 | / | 680 | )^ | 0.35 | + | 264369.7015
| DC = | 680 | * ( | 3410.2842 | [8 empty] | )*( | 5.1471 |  |  | )^ | 0.35 | + | 264369.7015
| DC = | 680 | * ( | 3410.2842 | [8 empty] | )*( | 1.7744 |  |  | ) |  | + | 264369.7015
| DC = | 4379136.0532 | for each reactor
| DC = | 4379136.0532 | for all reactors
Inflation Adjustment = |  |  | 1.35
| DC = | 5911833.6718

## ICC
Indirect Capital Costs
Total Direct Capital Costs, A | [9 empty] | 5911833.6718
Indirect Installation Costs
| General Facilities |  |  |  |  | 0.05 | A |  |  | 295591.6836
| Engineering and Home Office Fees |  |  |  |  | 0.1 | A |  |  | 591183.3672
| Process Contingencies |  |  |  |  | 0.05 | A |  |  | 295591.6836
Total Indirect Installation Costs, B |  | Retrofit factor = |  | 1 | * | 0.2 | A = | 0.2 | A = | 1182366.7344
| Project Contingency, C = | Retrofit factor = |  | 1 | * | 0.15 | (A+B) = | 0.15 | (A+B) = | 1064130.0609
Total Plant Cost D = | [7 empty] | A+B+C |  | 8158330.4671
| Allowance for Funds During Construction, E = | [5 empty] | 0 |  |  | 0
| Royalty Allowance, F = | [5 empty] | 0 |  |  | 0
| Preproduction Cost, G = | [5 empty] | 0.02 | (D+E) |  | 163166.6093
Inventory Capital, H =
| Initial Catalyst and Chemicals, I = | 0.058 | /lb * | 336.2707 | lb/r * | 24 | hr/day * | 14 | days = | 6553.2429
Total Capital Investment TCI = D+G+H | [7 empty] | +D+E+F+G+H+I |  | 8328050.3194
[8 empty] | Cost/kW = |  | 122.4713

## Ann Cost
Annual Costs
2.45 | DAC = Annual Maintenance Cost + Annual Reagent Cost + Annual Electricity Cost + Annual Water Cost + Annual Catalyst Cost
| 2.46 | Annual Maintenance Cost = 0.015 TCI
| Annual Maintenance Cost = | 0.015 | * | 8328050.3194
| Annual Maintenance Cost = | 124920.7548
| 2.47 | Annual Reagent Cost = qreagentCostreagenttop
| 2.47a | top = CFtotal8760hr/yr
| top = | 31.37% | * | 8760
| top = | 2748.2066
| Annual Reagent Cost = | 336.2707 | * | 2748.2066 | * | 0.058
| Annual Reagent Cost = | 53600.1946
| 2.49 | Annual Electricity Cost = Power (Costelect)top
| 2.48 | Power = 0.105QB[NOxinηNOx + 0.5(ΔPduct + ntotalΔPcatalyst)]
| Power = | 0.105 | * | 680 | *( | 0.41 | * | 90% | + | 0.5 | * ( | 3 | + | 3 | * | 1 | ))
| Power = | 240.5466 | kW
| Annual Electricity Cost = | 240.5466 | * | 2748.2066 | * | 0.08
| Annual Electricity Cost = | 52885.7403
| 2.51 | Annual Catalyst Replacement Cost = (Catalyst Replacement Cost)FWF
| 2.5 | Catalyst Replacement Cost = nSCRVolcatalystCCreplace/Rlayer
| Catalyst Replacement Cost = | 1 | * | 3109.6532 | * | 85.0158 | / | 2
| Catalyst Replacement Cost = | 132184.8508
| 2.52 | FWF = i{1/[(1+i)Y-1]}
| 2.53 | Y = hcatalyst/hyear
| Y = | 24000 | /( | 100% | * | 8760 | )
| Y = | 2.7397
| FWF = | 0.07 | *( | 1 | /( | 1 | + | 0.07 | )^ | 3 | - | 1 | )
| FWF = | 0.07 | *( | 1 | /( | 1.07 |  |  | )^ | 3 | - | 1 | )
| FWF = | 0.07 | *( | 1 | /( | 1.225 |  |  |  |  | - | 1 | )
| FWF = | 0.07 | *( | 1 | /( |  |  | 0.22504 |  |  |  |  | )
| FWF = | 0.31105
| Annual Catalyst Cost = | 41116.318
| DAC = | 272523.0077
| 2.55 | CRF = i(1+i)n/[(1+i)n-1]
| CRF = | 0.07 | *( | 1 | + | 0.07 | )^ | 20 | /(( | 1 | + | 0.07 | )^ | 20 | - | 1 | )
| CRF = | 0.07 | *( | 1.07 |  |  | )^ | 20 | /(( | 1.07 |  |  | )^ | 20 | - | 1 | )
| CRF = | 0.07 | *( | 3.8697 |  |  |  | ) | /(( | 3.8697 |  |  | ) |  | - | 1 | )
| CRF = | 0.07 | *( | 3.8697 |  |  |  | ) | /(( | 2.8697 |  |  | )
| CRF = | 0.094393
| Indirect Annual Cost = | CFR | * | TCI
| Indirect Annual Cost = | 0.094393 | * | 8328050.3194
| Indirect Annual Cost = | 786109.0354
| 2.56 | Total Annual Cost = Direct Annual Cost + Indirect Annual Cost
| Total Annual Cost = | 272523.0077 | + | 786109.0354
| Total Annual Cost = | 1058632.0431
| 2.57 | NOx Removed = NOxinηNOxQBtop
| NOx Removed = | 0.41 | * | 90% | * | 680 | * | 2748.2066 | / | 2000
| NOx Removed = | 344.79
| 2.58 | Cost effectiveness = TAC/NOx removed
| SCR Cost effectiveness ($/ton) = | 3070.3676
| Greatest dv improvement = | 0.85
| SCR Cost effectiveness ($/dv) = | 1245449.4625
| Cumulative dv improvement = | 2.3
| SCR Cost effectiveness ($/dv) = | 460274.8013

## Viz Tbl
Mill | High (dv)
Class I Area | Mill | PB #1+#2
Acadia NP | 3.7 | 2.8
Great Gulf WA | 2.2 | 1.7
Lye Brook WA | 1
Moosehorn WA | 1.7 | 1.3
Presidential Range-Dry River WA | 2.9 | 2.3
Roosevelt Campobello IP | 1.6
| 13.1 | 8.1
PB #1+#2 | High (dv) |  |  |  | Improvement (dv)
Class I Area | 0.7% S | WS | SCR | SNCR | 0.7% S | WS | SCR | SNCR
Acadia NP | 1.9 | 1.3 | 1.1 | 1.4 | 0.9 | 1.5 | 1.7 | 1.4
Great Gulf WA | 1 |  | 0.8 | 0.7 | 0.7 |  | 0.9 | 1
Lye Brook WA
Moosehorn WA | 0.7 | 0.3 | 0.6 | 0.6 | 0.6 | 1 | 0.7 | 0.7
Presidential Range-Dry River WA | 1.3 | 0.8 | 1 | 1.1 | 1 | 1.5 | 1.3 | 1.2
Roosevelt Campobello IP
| 4.9 | 2.4 | 3.5 | 3.8 | 3.2 | 4 | 4.6 | 4.3