## GivenAssume
Androscoggin Power Boilers #1 & #2
Given/Assumptions
Generation capacity (MW) | 68 | estimated
Fuel High Heating Value (Btu/gal) | 150000 | company report
Maximum Fuel Consumption Rate (gal/hr) | 4533.3333 | calculated | 680 | mmBtu/hr from company report
Maximum Annual Fuel Consumption (gal) | 39712000 | calculated
Maximum Annual Heat Input (mmBtu) | 5956800 | calculated
Actual annual heat input (mmBtu) | 1868780.4878 | calculated
Number of SNCR Operating Days | 365 | OAQPS Control Cost Manual
Uncontrolled NOx Concentration (lb/mmBtu) | 0.41 | company report
Uncontrolled NOx Emissions (tpy) | 383.1 | company report
Required Controlled NOx Concentration (lb/mmBtu) | 0.2665 | calculated
ash product (Btu/mmBtu) | 77000 | OAQPS Control Cost Manual
Stored Urea Concentration | 50% | OAQPS Control Cost Manual
Injected Urea Concentration | 10% | OAQPS Control Cost Manual
Reagent Heat of vaporization Hv (lb/Btu) | 900 | OAQPS Control Cost Manual
Reagent Molecular Weight (g/mole) | 60.06 | OAQPS Control Cost Manual
SRT | 2 | OAQPS Control Cost Manual
Reagent Density (lb/ft3 @ 60F) | 71 | OAQPS Control Cost Manual
Reagent Specific Volume (gal/ft3) | 7.481 | OAQPS Control Cost Manual
NOx Molecular Weight (g/mole) | 46.01 | OAQPS Control Cost Manual
Number of Days of Storage for Urea | 14 | OAQPS Control Cost Manual
Equipment Life (years) | 20 | OAQPS Control Cost Manual
Annual Interest Rate | 7% | OAQPS Control Cost Manual
Inflation Since 1998 | 1.35 | CEPCI 2007/CEPCI 1998
Water Consumption Cost ($/gal) | 0.0004 | OAQPS Control Cost Manual
Electrical Power Cost ($/kWh) | 0.08 | company report
50% Urea Solution Cost ($/gal) | 1.25 | company report
Oil Cost ($/mmBtu) | 6.71 | company report
Ash Disposal Cost ($/ton) |  | OAQPS Control Cost Manual

## Boiler Calcs
Boiler Calculations
1.3 QB = HVm-dotfuel
QB = | 150000 | Btu/lb * | 4533.3333 | lb/hr
QB = | 680 | mmBtu/hr
1.7 | CFPlant = actual mfuel/maximum mfuel
CFPlant = | 1868780.4878 | lb/yr / | 5956800
CFPlant = | 31.37%
1.8 | CFSNCR = tSCR/365 days
CFSCR = | 365 | days/ | 365 | days
CFSCR = | 100%
1.6 | CFTotal = CFPlant x CFSNCR
CFTotal = | 31.37% | * | 100%
CFTotal = | 31.37%
1.9 | ηNOx = (NOxin – NOxout) / NOxin
ηNOx = | ( | 0.41 | lb/mmBtu - | 0.2665 | lb/mmBtu)/ | 0.41 | lb/mmBtu
ηNOx = | 35%
Uncontrolled NOx emissions (tpy) |  |  | 383.1

## Reagent
Reagent Calculations
1.14 | NSR = [2NOxin – 0.7] ηNOx/ NOxin
NSR = | ( | 2 | * | 0.41 | + | 0.7 | ) | * | 35% | / | 0.41
NSR = | 1.2976
1.13 | Utilization = ηNOx/NSR
Utilization = | 26.97%
1.15 | m-dotreagent = NOxinQBηNOxNSR Mreagent/MNOx/SRT
| m-dotreagent = | 0.41 | * | 680 | * | 35% | * | 129.8% | * | 60.06 | / | 2 | / | 46.01
| m-dotreagent = | 82.6403 | lb/hr
1.16 | m-dotsol = m-dotreagent/Csol
| m-dotsol = | 82.6403 | / | 0.5
| m-dotsol = | 165.2805 | lb/hr
1.17 | qsol = m-dotvol/ρsol
| qsol = | 165.2805 | * | 7.481 | / | 71
| qsol = | 17.415 | gph
2.35 | Tank Volume = qsolt
| Tank Volume = | 17.415 | * | 14 | * | 24
| Tank Volume = | 5851.4334 | gal

## DCC
Direct Capital Cost
|  | 1.19 | DC = ($950/mmBtu/hr) * QB(mmBtu/hr)[(2375/mmBtu/hr)/QB(mmBtu/hr]0.577 * (0.66 + 0.85* ηNOx)
|  | DC = | 950 | * | 680 | *( | 2375 | / | 680 | )^ | 0.577 | *( | 0.66 | + | 0.85 | * | 35% | )
|  | DC = | 1272833.4009
Inflation Adjustment = |  |  | 1.35
| DC = | 1718325.0912

## ICC
Indirect Capital Costs
Total Direct Capital Costs, A |  |  |  | 1272833.4009
Indirect Installation Costs
| General Facilities | 0.05 | A | 63641.67
| Engineering and Home Office Fees | 0.1 | A | 127283.3401
| Process Contingencies | 0.05 | A | 63641.67
Total Indirect Installation Costs, B |  | 0.2 | A | 254566.6802
| Project Contingency, C = | 0.15 | (A+B) | 229110.0122
Total Plant Cost D = |  |  | A+B+C | 1756510.0932
| Preproduction Cost | 0.02 | D | 35130.2019
| Inventory Capital |  |  | 7314.2918
Total Capital Investment TCI = D+G+H |  |  | +D+E+F+G+H+I | 1798954.5868
|  |  | Cost/kW = | 26.4552

## Ann Cost
Annual Costs
2.45 | DAC = Annual Maintenance Cost + Annual Reagent Cost + Annual Electricity Cost + Annual Water Cost + Annual Catalyst Cost
| 2.46 | Annual Maintenance Cost = 0.015 TCI
| Annual Maintenance Cost = | 0.015 | * | 1798954.5868
| Annual Maintenance Cost = | 26984.3188
| 1.22 | Annual Reagent Cost = qsolCostreagenttop
| 1.22.a | top = CFtotal8760hr/yr
| top = | 31.37% | * | 8760
| top = | 2748.2066
| Annual Reagent Cost = | 17.415 | * | 1.25 | * | 2748.2066
| Annual Reagent Cost = | 59824.9551
| 1.24 | Annual Electricity Cost = Power (Costelect)top
| 1.23 | Power = 0.47NOxinNSRQB/9.5
| Power = | 0.47 | * | 0.41 | * | 1.2976 | * | 680 | / | 9.5
| Power = | 17.8976 | kW
| Annual Electricity Cost = | 17.8976 | * | 2748.2066 | * | 0.08
| Annual Electricity Cost = | 3934.9042
| 1.27 | Annual Water Cost = qwaterCostwater top
| 1.25 | qwater = m-dotsol/ρwater[Cureastored/Curea sol inj -1]
| qwater = | 165.2805 | / | 8.345 | *( | 50% | / | 10% | - | 1 | )
| qwater = | 79.2237
| Annual Water Cost = | 79.2237 | * | 0.0004 | * | 2748.2066
| Annual Water Cost = | 87.0893
| 1.31 | Annual ΔCoal cost = ΔCoal costcoal top
| 1.28 | ΔCoal(Btu/hr) = Hv(Btu/lb)* m-dotreagent(lb/hr)[1/ Curea sol inj -1]
| ΔCoal(Btu/hr) = | 900 | * | 165.2805 | *( | 1 | / | 10% | - | 1 | )
| ΔCoal(Btu/hr) = | 1338772.2533
| Annual ΔCoal cost = | 1.3388 | * | 6.71 | * | 2748.2066
| Annual ΔCoal cost = | 24687.5846
| 1.32 | Annual ΔAsh cost = ΔAsh costash top
| 1.3 | ΔAsh = ΔCoal ash product/HHV
| ΔAsh = | 1.3388 | * | 77000 | / | 150000
| ΔAsh = | 0.68724
| Annual ΔAsh cost = | 0.68724 | * | 0 | * | 2748.2066 | / | 2000
| Annual ΔAsh cost = | 0
| Total Variable Cost = | 88534.5332
| Total Direct Annual Cost = | 26984.3188 | + | 88534.5332
| Total Direct Annual Cost = | 115518.852
| 1.34 | CRF = i(1+i)n/[(1+i)n-1]
| CRF = | 0.07 | *( | 1 | + | 0.07 | )^ | 20 | /(( | 1 | + | 0.07 | )^ | 20 | - | 1 | )
| CRF = | 0.07 | *( | 1.07 |  |  | )^ | 20 | /(( | 1.07 |  |  | )^ | 20 | - | 1 | )
| CRF = | 0.07 | *( | 3.8697 |  |  |  | ) | /(( | 3.8697 |  |  | ) |  | - | 1 | )
| CRF = | 0.07 | *( | 3.8697 |  |  |  | ) | /(( | 2.8697 |  |  | )
| CRF = | 0.094393
| 1.33 | IDAC = CRF*TCI
| Indirect Annual Cost = | 0.094393 | * | 1798954.5868
| Indirect Annual Cost = | 169808.5867
| 1.35 | Total Annual Cost = Direct Annual Cost + Indirect Annual Cost
| Total Annual Cost = | 115518.852 | + | 169808.5867
| Total Annual Cost = | 285327.4387
| 1.36 | NOx Removed = NOxinηNOxQBtop
| NOx Removed = | 0.41 | * | 35% | * | 680 | * | 2748.2066 | / | 2000
| NOx Removed = | 134.085
| 1.37 | Cost effectiveness = TAC/NOx removed
| Cost effectiveness = | 2127.9594
| Greatest dv improvement = | 0.7
| SNCR Cost effectiveness ($/dv) = | 407610.6267
| Cumulative dv improvement = | 2.15
| SNCR Cost effectiveness ($/dv) = | 132710.4366

## Viz Tbl
Mill | High (dv)
Class I Area | Mill | PB #1+#2
Acadia NP | 3.7 | 2.8
Great Gulf WA | 2.2 | 1.7
Lye Brook WA | 1
Moosehorn WA | 1.7 | 1.3
Presidential Range-Dry River WA | 2.9 | 2.3
Roosevelt Campobello IP | 1.6
| 13.1 | 8.1
PB #1+#2 | High (dv) |  |  |  | Improvement (dv)
Class I Area | 0.7% S | WS | SCR | SNCR | 0.7% S | WS | SCR | SNCR
Acadia NP | 1.9 | 1.3 | 1.1 | 1.4 | 0.9 | 1.5 | 1.7 | 1.4
Great Gulf WA | 1 |  | 0.8 | 0.7 | 0.7 |  | 0.9 | 1
Lye Brook WA
Moosehorn WA | 0.7 | 0.3 | 0.6 | 0.6 | 0.6 | 1 | 0.7 | 0.7
Presidential Range-Dry River WA | 1.3 | 0.8 | 1 | 1.1 | 1 | 1.5 | 1.3 | 1.2
Roosevelt Campobello IP
| 4.9 | 2.4 | 3.5 | 3.8 | 3.2 | 4 | 4.6 | 4.3