## Sheet1
Boiler No. 3 |  | Boiler No. 4
% Sulfur | Annual Costs | % Sulfur | Annual Costs
1 | $0.68 million | 0.5 | $9.2 million
0.7 | $0.80 million | 0.3 | $18.3 million
0.5 | $3.2 million | -- | --
0.3 | $5.7 million | -- | --

## Sheet2
% Sulfur | Average Cost Effectiveness ($/ton SO2 Removed) | Incremental Cost | Incremental Cost Effectiveness ($/ton SO2 Removed)
1 | 2189 | -- | --
0.7 | 1234 | $0.12 million | 354
0.5 | 3700 | $2.44 million | 10808
0.3 | 5156 | $2.44 million | 10808
% Sulfur | Average Cost Effectiveness ($/ton SO2 Removed) | Incremental Cost | Incremental Cost Effectiveness ($/ton SO2 Removed)
0.5 | 27952 | -- | --
0.3 | 15835 | $9.1 5 million | $1 1,046

## Tbl 3-7 & 3-8
TABLE 3-7
VISIBILITY IMPACT RANKINGS AT PSD CLASS I AREAS
FPL ENERGY WYMAN UNIT NO. 3
Fuel Sulfur Content | 1.6% | 1% | 0.7% | 0.5% | 0.3%
Acadia National Park | 3.36 | 2.37 | 1.93 | 1.58 | 1.21
Great Gulf Widerness Area | 1.23 | 0.87 | 0.7 | 0.58 | 0.47
Lye Brook Wilderness Area | 0.49 | 0.38 | 0.25 | 0.2 | 0.14
Moosehorn Wilderness Area | 1.46 | 0.99 | 0.77 | 0.61 | 0.46
Presidential Range-Dry River Wilderness Area | 1.76 | 1.54 | 1.07 | 0.9 | 0.73
Roosevelt Carnpobello International Park | 1.43 | 0.97 | 0.75 | 0.6 | 0.44
Cumulative Impacts | 9.73 | 7.12 | 5.47 | 4.47 | 3.45
TABLE 3-8
VISIBILITY IMPACT RANKINGS AT PSD CLASS I AREAS
FPL ENERGY WYMAN UNIT NO. 4
Fuel Sulfur Content |  |  | 0.7% | 0.5% | 0.3%
Acadia National Park |  |  | 3.14 | 2.73 | 2.3
Great Gulf Widerness Area |  |  | 1.55 | 1.31 | 1.06
Lye Brook Wilderness Area |  |  | 0.74 | 0.6 | 0.44
Moosehorn Wilderness Area |  |  | 1.7 | 1.41 | 1.09
Presidential Range-Dry River Wilderness Area |  |  | 1.95 | 1.7 | 1.38
Roosevelt Carnpobello International Park |  |  | 1.56 | 1.29 | 0.99
Cumulative Impacts |  |  | 10.64 | 9.04 | 7.26

## Tbl 5-2
TABLE 5-2
SO2 CONTROL TECHNOLOGY FEASIBILITY ANALYSIS -BOILER NOS. 3 AND 4
|  | Technically | Rank Based on | Rank Based on
| Estimated | Feasible and | Control | Project
SO2 Abatement Method | Efficiency | Demonstrated? | Efficiency | Suitability
Low-sulfur (0.05, 0.0015%) No. 2 Fuel Oil | 98% | Yes | 1 | 2
Reduced sulfur (l%, 0.7%, 0.5%) No. 6 Fuel Oil | 30-50% | Yes | 4 | 1
Wet Scrubbers | >90% | Yes | 2 | 3
Dry Scrubbers | 60-95% | No | 3 | 4

## Tbl 5-3
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 -2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
Unit 4 | 1035313 | 524077 | 666785 | 56017 | 323562 | 140505 | 779695 | 595431 | 361401 | 189790 | 232034
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
Unit 4 | 10027949 | 4943088 | 6382955 | 577749 | 3,2 12,458 | 1559476 | 7485519 | 5663022 | 3480352 | 1895104 | 2385967
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
Unit 4 | 66853 | 32954 | 42553 | 3852 | 21416 | 10397 | 49903 | 37753 | 23202 | 12634 | 15906
| Capacitv Factor | [5 empty] | 2-Year Average Capacity Factor
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 20.9% | 17.4% | 21.7% | 1.5% | 6.6% | 3.3% | 19.1% | 19.6% | 11.6% | 4.1% | 4.9%
Unit 4 | 18.2% | 9% | 11.6% | 1% | 5.8% | 2.8% | 13.6% | 10.3% | 6.3% | 3.4% | 4.3%
| SO2 Emissions | [5 empty] | 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1149.1 | 1383 | 1499.8 | 74.9 | 452.5 | 255.1 | 1266.1 | 1441.4 | 787.4 | 263.7 | 353.8
Unit 4 | 3226.7 | 1569.6 | 1992.1 | 170.6 | 1050.2 | 574.8 | 2398.2 | 1780.9 | 1081.4 | 610.4 | 812.5
EPA Clean Air Market Acid Rain database.
Based on annual heat input and assuming 150,000 Btu/gallon. 'Based on annual heat input and maximum heat input rates of 1,190 MMBtu/hr and 6,290 MMBtu/hr for Boiler Nos. 3 and 4, respectively.

## Tbl 5-3 (2%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 - 2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
| Annual Fuel Cost for |  | 2 | %S #6 @ | 11.63 | /mmBtu | 2-Year Average Fuel Cost for | 2 | %S #6 @ | 11.63 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 25285364.5 | 21116951.53 | 25130452.9 | 1812361.05 | 8013407.27 | 3979599.92 | 23201163.83 | 23705208.03 | 14052912.79 | 4912884.16 | 5996509.41
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
| Capacitv Factor | [5 empty] | 2-Year Average Capacity Factor
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 20.9% | 17.4% | 21.7% | 1.5% | 6.6% | 3.3% | 19.1% | 19.6% | 11.6% | 4.1% | 4.9%
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 2275.558 | 1900.485 | 2366.304 | 163.123 | 721.258 | 358.117 | 2088.1 | 2133.473 | 1264.792 | 442.112 | 539.609

## Tbl 5-3 (1.6%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 - 2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
| Annual Fuel Cost for |  | 1.6 | %S #6 @ |  | /mmBtu | 2-Year Average Fuel Cost for | 1.6 | %S #6 @ | 0 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
| Capacitv Factor | [5 empty] | 2-Year Average Capacity Factor
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 20.9% | 17.4% | 21.7% | 1.5% | 6.6% | 3.3% | 19.1% | 19.6% | 11.6% | 4.1% | 4.9%
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1820.4464 | 1520.388 | 1893.0432 | 130.4984 | 577.0064 | 286.4936 | 1670.48 | 1706.7784 | 1011.8336 | 353.6896 | 431.6872
Cumulative Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73

## Tbl 5-3 (1%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 -2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
| Annual Fuel Cost for |  | 1 | %S #6 @ | 11.97 | /mmBtu | 2-Year Average Fuel Cost for | 1 | %S #6 @ | 11.97 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 26024575.5 | 21734300.07 | 25865135.1 | 1865344.95 | 8247677.13 | 4095942.48 | 23879443.77 | 24398223.57 | 14463746.01 | 5056511.04 | 6171815.79
| Increased Annual Fuel Cost for |  | 1 | %S #6 @ | 11.97 | /mmBtu | Increased 2-Year Average Fuel Cost for | 1 | %S #6 @ | 11.97 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 739211 | 617348.54 | 734682.2 | 52983.9 | 234269.86 | 116342.56 | 678279.94 | 693015.54 | 410833.22 | 143626.88 | 175306.38
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1137.779 | 950.2425 | 1183.152 | 81.5615 | 360.629 | 179.0585 | 1044.05 | 1066.7365 | 632.396 | 221.056 | 269.8045
| Calculated SO2 Emissions Reductions | [5 empty] | Calculated 2-Year Average SO2 Emissions Reductions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1137.779 | 950.2425 | 1183.152 | 81.5615 | 360.629 | 179.0585 | 1044.05 | 1066.7365 | 632.396 | 221.056 | 269.8045
| Calculated SO2 Reductions Cost-Effectiveness ($/ton) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/ton)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 649.6965 | 649.6747 | 620.9534 | 649.619 | 649.6146 | 649.7461 | 649.6623 | 649.6595 | 649.6455 | 649.7307 | 649.7534
Greatest Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36
Greatest Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 746677.7778 | 623584.3838 | 742103.2323 | 53519.0909 | 236636.2222 | 117517.7374 | 685131.2525 | 700015.697 | 414983.0505 | 145077.6566 | 177077.1515
Cumulative Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73
Cumulative Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 283222.6054 | 236532.0077 | 281487.433 | 20300.3448 | 89758.567 | 44575.6935 | 259877.3716 | 265523.1954 | 157407.364 | 55029.4559 | 67167.1954

## Tbl 5-3 (0.7%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 -2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
Unit 4 | 1035313 | 524077 | 666785 | 56017 | 323562 | 140505 | 779695 | 595431 | 361401 | 189790 | 232034
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
Unit 4 | 10027949 | 4943088 | 6382955 | 577749 | 3212458 | 1559476 | 7485519 | 5663022 | 3480352 | 1895104 | 2385967
| Annual Fuel Cost for |  | 0.7 | %S #6 @ | 12.03 | /mmBtu | 2-Year Average Fuel Cost for | 0.7 | %S #6 @ | 12.03 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 26155024.5 | 21843243.93 | 25994784.9 | 1874695.05 | 8289018.87 | 4116473.52 | 23999140.23 | 24520520.43 | 14536245.99 | 5081856.96 | 6202752.21
Unit 4 | 120636226.47 | 59465348.64 | 76786948.65 | 6950320.47 | 38645869.74 | 18760496.28 | 90050793.57 | 68126154.66 | 41868634.56 | 22798101.12 | 28703183.01
| Increased Annual Fuel Cost for |  | 0.7 | %S #6 @ | 12.03 | /mmBtu | Increased 2-Year Average Fuel Cost for | 0.7 | %S #6 @ | 12.03 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 869660 | 726292.4 | 864332 | 62334 | 275611.6 | 136873.6 | 797976.4 | 815312.4 | 483333.2 | 168972.8 | 206242.8
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
Unit 4 | 66853 | 32954 | 42553 | 3852 | 21416 | 10397 | 49903 | 37753 | 23202 | 12634 | 15906
| Capacitv Factor | [5 empty] | 2-Year Average Capacity Factor
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 20.9% | 17.4% | 21.7% | 1.5% | 6.6% | 3.3% | 19.1% | 19.6% | 11.6% | 4.1% | 4.9%
Unit 4 | 18.2% | 9% | 11.6% | 1% | 5.8% | 2.8% | 13.6% | 10.3% | 6.3% | 3.4% | 4.3%
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 796.4453 | 665.1698 | 828.2064 | 57.093 | 252.4403 | 125.341 | 730.835 | 746.7156 | 442.6772 | 154.7392 | 188.8631
Unit 4 | 3673.5723 | 1810.8223 | 2338.2874 | 211.6674 | 1176.8092 | 571.3152 | 2742.1699 | 2074.5273 | 1274.9499 | 694.2383 | 874.0347
| Calculated SO2 Emissions Reductions | [5 empty] | Calculated 2-Year Average SO2 Emissions Reductions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1479.1127 | 1235.3153 | 1538.0976 | 106.0299 | 468.8177 | 232.776 | 1357.265 | 1386.7575 | 822.1148 | 287.3728 | 350.7459
| Calculated SO2 Reductions Cost-Effectiveness ($/ton) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/ton)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 587.9606 | 587.9409 | 561.9487 | 587.8905 | 587.8865 | 588.0055 | 587.9297 | 587.9272 | 587.9145 | 587.9916 | 588.0121
Greatest Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36
Greatest Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 608153.8462 | 507896.7832 | 604427.972 | 43590.2098 | 192735.3846 | 95715.8042 | 558025.4545 | 570148.5315 | 337995.2448 | 118162.7972 | 144225.7343
Cumulative Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73
Cumulative Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 204145.5399 | 170491.1737 | 202894.8357 | 14632.3944 | 64697.5587 | 32129.9531 | 187318.4038 | 191387.8873 | 113458.4977 | 39664.9765 | 48413.8028

## Tbl 5-3 (0.5%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 -2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
Unit 4 | 1035313 | 524077 | 666785 | 56017 | 323562 | 140505 | 779695 | 595431 | 361401 | 189790 | 232034
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
Unit 4 | 10027949 | 4943088 | 6382955 | 577749 | 3212458 | 1559476 | 7485519 | 5663022 | 3480352 | 1895104 | 2385967
| Annual Fuel Cost for |  | 0.5 | %S #6 @ | 13.25 | /mmBtu | 2-Year Average Fuel Cost for | 0.5 | %S #6 @ | 13.25 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 28807487.5 | 24058435.75 | 28630997.5 | 2064813.75 | 9129634.25 | 4533938 | 26432968.25 | 27007223.25 | 16010412.25 | 5597224 | 6831792.75
Unit 4 | 132870324.25 | 65495916 | 84574153.75 | 7655174.25 | 42565068.5 | 20663057 | 99183126.75 | 75035041.5 | 46114664 | 25110128 | 31614062.75
| Increased Annual Fuel Cost for |  | 0.5 | %S #6 @ | 13.25 | /mmBtu | Increased 2-Year Average Fuel Cost for | 0.5 | %S #6 @ | 13.25 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 3522123 | 2941484.22 | 3500544.6 | 252452.7 | 1116226.98 | 554338.08 | 3231804.42 | 3302015.22 | 1957499.46 | 684339.84 | 835283.34
Unit 4 | 12234097.78 | 6030567.36 | 7787205.1 | 704853.78 | 3919198.76 | 1902560.72 | 9132333.18 | 6908886.84 | 4246029.44 | 2312026.88 | 2910879.74
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
Unit 4 | 66853 | 32954 | 42553 | 3852 | 21416 | 10397 | 49903 | 37753 | 23202 | 12634 | 15906
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 568.8895 | 475.1212 | 591.576 | 40.7807 | 180.3145 | 89.5293 | 522.025 | 533.3682 | 316.198 | 110.528 | 134.9023
Unit 4 | 2623.9803 | 1293.4445 | 1670.2052 | 151.191 | 840.578 | 408.0822 | 1958.6927 | 1481.8052 | 910.6785 | 495.8845 | 624.3105
| Calculated SO2 Emissions Reductions | [5 empty] | Calculated 2-Year Average SO2 Emissions Reductions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1706.6685 | 1425.3637 | 1774.728 | 122.3423 | 540.9435 | 268.5878 | 1566.075 | 1600.1047 | 948.594 | 331.584 | 404.7067
Unit 4 | 1049.5921 | 517.3778 | 668.0821 | 60.4764 | 336.2312 | 163.2329 | 783.4771 | 592.7221 | 364.2714 | 198.3538 | 249.7242
| Calculated SO2 Reductions Cost-Effectiveness ($/ton) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/ton)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 2063.7417 | 2063.6727 | 1972.4401 | 2063.4956 | 2063.4816 | 2063.8993 | 2063.6332 | 2063.6244 | 2063.5798 | 2063.8506 | 2063.9224
Unit 4 | 11656.0498 | 11656.0227 | 11656.0601 | 11655.0221 | 11656.2614 | 11655.4979 | 11656.1584 | 11656.1992 | 11656.2251 | 11656.0756 | 11656.3783
Greatest Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36
Unit 4 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
Greatest Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78
Unit 4 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1978720.7865 | 1652519.2247 | 1966598.0899 | 141827.3596 | 627093.809 | 311425.8876 | 1815620.4607 | 1855064.7303 | 1099718.7978 | 384460.5843 | 469260.3034
Unit 4 | 29839262.878 | 14708700.878 | 18993183.1707 | 1719155.561 | 9559021.3659 | 4640392 | 22273983.3659 | 16850943.5122 | 10356169.3659 | 5639089.9512 | 7099706.6829
Cumulative Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73
Unit 4 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64
Cumulative Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26
Unit 4 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 669605.1331 | 559217.5323 | 665502.7757 | 47994.8099 | 212210.4525 | 105387.4677 | 614411.4867 | 627759.5475 | 372148.1863 | 130102.6312 | 158799.1141
Unit 4 | 7646311.1125 | 3769104.6 | 4867003.1875 | 440533.6125 | 2449499.225 | 1189100.45 | 5707708.2375 | 4318054.275 | 2653768.4 | 1445016.8 | 1819299.8375

## Tbl 5-3 (0.3%S)
TABLE 5-3 FPL ENERGY WYMAN STATION ACTUAL FUEL USAGE. 2003 -2008
| Gross Generation | [5 empty] | 2-Year Average Generation
Unit | 2003 (MWh) | 2004 (MWh) | 2005 (M\Vh) | 2006 (MWh) | 2007 (MWh) | 2008 (MWh) | 2003-2004 (MWh) | 2004-2005 (MWh) | 2005-2006 (MWH) | 2006-2007 (MWh) | 2007-2008 (MWh)
Unit 3 | 218284 | 186518 | 230208 | 13149 | 66469 | 29796 | 202401 | 208363 | 121679 | 39809 | 48133
Unit 4 | 1035313 | 524077 | 666785 | 56017 | 323562 | 140505 | 779695 | 595431 | 361401 | 189790 | 232034
| Annual Heat Input | [5 empty] | 2-Year Average Heat Input
Unit | 2003 (MMBtu) | 2004 (MMBtu) | 2005 (MMBtu) | 2006 (MMBtu) | 2007 (MMBtu) | 2008 (MMBtu) | 2003-2003 (MMBtu) | 2004-2005 (blMBtu) | 2005-2006 (MMBtu) | 2006-2007 (MMBtu) | 2007-2008 (MMBtu)
Unit 3 | 2174150 | 1815731 | 2160830 | 155835 | 689029 | 342184 | 1994941 | 2038281 | 1208333 | 422432 | 515607
Unit 4 | 10027949 | 4943088 | 6382955 | 577749 | 3212458 | 1559476 | 7485519 | 5663022 | 3480352 | 1895104 | 2385967
| Annual Fuel Cost for |  | 0.3 | %S #6 @ | 14.97 | /mmBtu | 2-Year Average Fuel Cost for | 0.3 | %S #6 @ | 14.97 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 32547025.5 | 27181493.07 | 32347625.1 | 2332849.95 | 10314764.13 | 5122494.48 | 29864266.77 | 30513066.57 | 18088745.01 | 6323807.04 | 7718636.79
Unit 4 | 150118396.53 | 73998027.36 | 95552836.35 | 8648902.53 | 48090496.26 | 23345355.72 | 112058219.43 | 84775439.34 | 52100869.44 | 28369706.88 | 35717925.99
| Increased Annual Fuel Cost for |  | 0.3 | %S #6 @ | 14.97 | /mmBtu | Increased 2-Year Average Fuel Cost for | 0.3 | %S #6 @ | 14.97 | /mmBtu
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003 - 2004 | 2004 - 2005 | 2005 - 2006 | 2006 - 2007 | 2007 - 2008
Unit 3 | 7261661 | 6064541.54 | 7217172.2 | 520488.9 | 2301356.86 | 1142894.56 | 6663102.94 | 6807858.54 | 4035832.22 | 1410922.88 | 1722127.38
Unit 4 | 29482170.06 | 14532678.72 | 18765887.7 | 1698582.06 | 9444626.52 | 4584859.44 | 22007425.86 | 16649284.68 | 10232234.88 | 5571605.76 | 7014742.98
| Annual Fuel Usage | [5 empty] | 2-Year Average Fuel Usage
Unit | 2003 (10^3 gal/yr) | 2004 (10^3 gal/yr) | 2005 (10^3 gal/yr) | 2006 (10^3 gal/yr) | 2007 (10^3 gal/yr) | 2008 (10^3 gal/yr) | 2003-2004 (10^3 gal/yr) | 2004-2005 (10^3 gal/yr) | 2005-2006 (10^3 gal/yr) | 2006-2007 (10^3 gal/yr) | 2007-2008 (10^3 gal/yr)
Unit 3 | 14494 | 12105 | 15072 | 1039 | 4594 | 2281 | 13300 | 13589 | 8056 | 2816 | 3437
Unit 4 | 66853 | 32954 | 42553 | 3852 | 21416 | 10397 | 49903 | 37753 | 23202 | 12634 | 15906
| Calculated SO2 Emissions | [5 empty] | Calculated 2-Year Average SO2 Emissions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 341.3337 | 285.0727 | 354.9456 | 24.4685 | 108.1887 | 53.7176 | 313.215 | 320.021 | 189.7188 | 66.3168 | 80.9413
Unit 4 | 1574.3881 | 776.0667 | 1002.1232 | 90.7146 | 504.3468 | 244.8493 | 1175.2157 | 889.0832 | 546.4071 | 297.5307 | 374.5863
| Calculated SO2 Emissions Reductions | [5 empty] | Calculated 2-Year Average SO2 Emissions Reductions
Unit | 2003 (TPY) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1934.2243 | 1615.4123 | 2011.3584 | 138.6546 | 613.0693 | 304.3995 | 1774.885 | 1813.4521 | 1075.0732 | 375.7952 | 458.6676
Unit 4 | 2099.1842 | 1034.7556 | 1336.1642 | 120.9528 | 672.4624 | 326.4658 | 1566.9542 | 1185.4442 | 728.5428 | 396.7076 | 499.4484
| Calculated SO2 Reductions Cost-Effectiveness ($/ton) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/ton)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 3754.3014 | 3754.1758 | 3588.2079 | 3753.8537 | 3753.8283 | 3754.5881 | 3754.104 | 3754.088 | 3754.0069 | 3754.4995 | 3754.6301
Unit 4 | 14044.5846 | 14044.5519 | 14044.597 | 14043.3463 | 14044.8396 | 14043.9196 | 14044.7154 | 14044.7646 | 14044.7958 | 14044.6156 | 14044.9804
Greatest Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36 | 3.36
Unit 4 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
Greatest Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15
Unit 4 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 3377516.7442 | 2820716.9953 | 3356824.2791 | 242087.8605 | 1070398.5395 | 531578.8651 | 3099117.6465 | 3166445.8326 | 1877131.2651 | 656243.2 | 800989.4791
Unit 4 | 35097821.5 | 17300808 | 22340342.5 | 2022121.5 | 11243603 | 5458166 | 26199316.5 | 19820577 | 12181232 | 6632864 | 8350884.5
Cumulative Visibility Impact (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73 | 9.73
Unit 4 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64
Cumulative Visibility Improvement (dv)
Unit | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2003-2004 | 2004-2005 | 2005-2006 | 2006-2007 | 2007-2008
Unit 3 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28
Unit 4 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| Calculated SO2 Reductions Cost-Effectiveness ($/dv) | [5 empty] | Calculated 2-Year Average SO2 Reductions Cost-Effectiveness ($/dv)
Unit | 2003 ($/ton) | 2004 (TPY) | 2005 (TPY) | 2006 (TPY) | 2007 (TPY) | 2008 (TPY) | 2003-2004 (TPY) | 2004-2005 (TPY) | 2005-2006 (TPY) | 2006-2007 (TPY) | 2007-2008 (TPY)
Unit 3 | 1156315.4459 | 965691.328 | 1149231.242 | 82880.3981 | 366458.0987 | 181989.5796 | 1061003.6529 | 1084053.9076 | 642648.4427 | 224669.2484 | 274224.1051
Unit 4 | 8722535.5207 | 4299609.0888 | 5552037.7811 | 502539.071 | 2794268.2012 | 1356467.2899 | 6511072.7396 | 4925823.8698 | 3027288.426 | 1648404.071 | 2075367.7456

## Sheet7
Wyman #3 (2007 - 2008)
Fuel Sulfur (%) | 1 | 0.7 | 0.5 | 0.3
Increased Annual Fuel Cost | 175306.38 | 206242.8 | 835283.34 | 1722127.38
SO2 Emission Reductions (tpy) | 269.8045 | 350.7459 | 404.7067 | 458.6676
SO2 Reductions Cost-Effectiveness ($/ton) | 649.7534 | 588.0121 | 2063.9224 | 3754.6301
Greatest Visibility Improvement (dv) | 0.99 | 1.43 | 1.78 | 2.15
Cost-Effectiveness ($/dv) | 177077.1515 | 144225.7343 | 469260.3034 | 800989.4791
Cumulative Visibility Improvement (dv) | 2.61 | 4.26 | 5.26 | 6.28
Cumulative Cost-Effectiveness ($/dv) | 67167.1954 | 48413.8028 | 158799.1141 | 274224.1051
Wyman #4 (2007 - 2008)
Fuel Sulfur (%) |  |  | 0.5 | 0.3
Increased Annual Fuel Cost |  |  | 2910879.74 | 7014742.98
SO2 Emission Reductions (tpy) |  |  | 249.7242 | 499.4484
SO2 Reductions Cost-Effectiveness ($/ton) |  |  | 11656.3783 | 14044.9804
Greatest Visibility Improvement (dv) |  |  | 0.41 | 0.84
Cost-Effectiveness ($/dv) |  |  | 7099706.6829 | 8350884.5
Cumulative Visibility Improvement (dv) |  |  | 1.6 | 3.38
Cumulative Cost-Effectiveness ($/dv) |  |  | 1819299.8375 | 2075367.7456

## Sheet3
% Sulfur | Ranked Visibility Impact | Visibility Cost Effectiveness ($/deciview) | Incremental Visibility Improvement | Incremental Visibility Cost Effectiveness ($/deciview)
1 | I st | $0.69 million | -- | --
| 8th | $1.95 million | -- | --
0.7 | I st | $0.56 million | 0.44 dv | $0.27 million
| 8th | $1.67 million | 0.13 dv | $0.92 million
0.5 | I st | $1.82 million | 0.35 dv | $6.97 million
| 8th | $5.41 million | 0.12 dv | $20.3 million
0.3 | I st | $2.64 million | 0.37 dv | $6.59 million
| 8th | $8.12 million | 0.10 dv | $24.4 million
% Sulfur | Ranked Visibility Impact | Visibility Cost Effectiveness ($/deciview) | Incremental Visibility Improvement | Incremental Visibility Cost Effectiveness ($/deciview)
0.5 | I st | $22.3 million | -- | --
| 8th | $39.8 million | -- | --
0.3 | I st | $19.5 million | 0.53 dv | $17.3 million
| 8th | $35.2 million | 0.29 dv | $3 1.6 million