## Form Instructions
Rev | 2023-11-01
Form Instructions
To Installers and Inspectors: This electronic document (the overall workbook and each individual inspection worksheet) is password protected so that formulas and function in certain cells cannot be changed outside of the DEP. If you find errors in this workbook, need something clarified, have a suggestion on how to improve the form, or would like to include your business logo or make a similar addition to the form, please contact the DEP at 207-287-7688 and ask to speak with someone in the Underground Tanks Unit.
General Instructions
1. | State law and Department of Environmental Protection (Department) rules require submittal of an inspection certifying all procedures and equipment are in compliance. The Department does not accept failing annual inspections.
Exceptions: Inspection failures for (1) Certified A/B Operator can be resolved by the owner by submitting a copy of a current and valid certificate; and (2) Failing cathodic protection (CP) results can be resolved by an installer or CP certified inspector retesting CP and attaining passing results within six months.
2. | A facility that fails to submit a passing annual inspection may be prohibited from receiving deliveries and dispensing product in accordance with Maine law 38 M.R.S. § 565-A. Items that are failing must be repaired or corrected within thirty (30) days or the owner must notify the Department.
3. | Leak detection equipment and procedures, spill and overfill prevention devices must be checked or tested annually for proper operation. Cathodically protected tanks and piping must be checked annually to insure they are adequately protected from corrosion.
4. | All work associated with testing of equipment and checking of procedures must be performed by or under the direct, onsite supervision of a Maine certified underground storage tank installer or a Maine certified underground storage tank inspector.
5. | Mail completed reports to: Annual Tank Inspections, Maine Department of Environmental Protection, 17 State House Station, Augusta, Maine 04333-0017 (physical address: 28 Tyson Drive, 04330) within thirty (30) days after the inspection is completed. The owner/operator must retain a copy.
6. | Detailed instructions on how to fill out this form are provided in the Department's “UST Inspector Reference Handbook”, available online at www.maine.gov/dep/waste/ust/pubs.html. The Annual Inspection Report form, the Inspector Reference Handbook and a list of Frequently Asked Questions (FAQ’s) are also available by calling the Underground Tanks Unit at (207) 287-7688.
SPECIAL INSTRUCTIONS
1 | General instructions covering Annual Inspection requirements are located in the Annual Inspection Owner/Operator Guide, a separate document. Instructions for completing the Annual Inspection Report form are located in the UST Inspector Reference Handbook. The special instructions contained in this page are designed to be used in conjunction with, and to enhance the instructions of, the Handbook. These instructions will also provide a guide to functions that are specific to this Microsoft Excel workbook.
2 | This workbook contains all pages of the Annual Inspection Report form (Page 1: Summary through Page 11: Annual Tightness Testing). It also contains two instruction pages and a copy of the Weekly Walkthrough Inspection Checklist and signage guidance for unattended fueling. Each page is accessed by clicking on the color-coded tabs at the bottom of the workbook: = Form Instructions (two printed pages) = Guidance Document (for facility owners and/or operators) = Page 1: Summary = Pages 2-11: Inspection Checklist worksheets
3 | Information can only be entered into cells (blocks) that are NOT shaded.
4 | On all pages, blocks that are shaded light yellow cannot be filled in by the user. These shaded blocks are automatically filled in by the Excel program based on other entrees made in the form. For example: A CTI inspects a facility with only one tank and finds that the tank's ball float is not set at 90% tank capacity. The CTI then places an "X" in appropriate FAIL block. The Excel program will then automatically place an "X" in the light-yellow "Overfill Prevention" FAIL box below and also place an "X" in the "Overfill Prevention" FAIL box for that tank on the Summary Page.
5 | Please use only the letter "X" when filling in any PASS, FAIL, Yes or No check-box. It doesn't matter if the "X" is capitalized or a small letter.
SUMMARY PAGE ONLY
6 | Much of the information that a user enters on Page 1, Summary Page is automatically copied into appropriate cells (blocks) in the separate worksheet checklists. For example, the facility registration number and inspection date are copied and placed on the top of each subsequent inspection page. The tank/chamber number, volume, and product contained in a tank are also copied and pasted into pages where the information is needed.
7 | Each PASS block on the Summary page must be manually filled in (of course, this is only if the appropriate section in the inspection page warrants a PASS on the summary page!)
WORKSHEET CHECKLISTS
8 | An "X" that is placed in any "FAIL" box in an individual inspection page (pages 3 through 11) will automatically update the appropriate overall "FAIL" boxes in the Summary Page (page 1).
9 | "Pass" blocks must be manually filled-in, where appropriate, on each page; there is NO automatic copying of any "Pass" to the Summary Page (page 1)
10 | Use the key sequence: <Alt> <Enter> to start a new line in any "Comments" block; using just the <Enter> key will close the editing session in the "Comments" block and move you to the next open fill-in block.
11 | If you need additional space for written comments, or in the case of page 6 where there is no comments section, use any other comments box on any page. Please start each comment with the inspection item number to which the comment refers.

## Weekly Walk-thru Insp Chklst
State of Maine
Department of Environmental Protection
Underground Oil Storage Facility - Class A/B Operator
Weekly Walk-Through Inspection Checklist
Facility Name & Reg # _______________________________ |  | Month / Year: |  | _______________________
|  | 1 | 2 | 3 | 4 | 5
Date of Inspection:
Release Detection:
● Is the Electronic system working properly? ● Is daily inventory being maintained and properly reconciled monthly? ● Is the Manual Groundwater or Tank Interstitial Space Log being maintained?
Electronic Overfill Alarm (if equipped): Inspect/test for proper operation. Can a fuel delivery person hear and see the alarm when it alarms?
Spill Log: Is the spill log properly used and maintained?
Spill Buckets: Are spill buckets clean and empty?
Spill And Overfill Response Supplies: Inventory the emergency spill response supplies. If the supplies are low, restock the supplies. Are supplies adequate?
Fill And Monitoring Ports: Inspect all fill, monitoring and vapor recovery ports. Are covers and caps tightly sealed with no damage?
Dispenser Area: Check the dispenser islands and surrounding areas. Are these areas free of evidence of spills and discharges? Clean areas as needed.
Dispensers And Dispenser Sumps: Open each dispenser cabinet and inspect all piping, fittings, and couplings for signs of leakage. Are the sumps free of any water, product or debris? (Remove any liquid or debris and disposed of properly)
Dispenser Hoses, Nozzles, and Breakaways: Are fittings tight and functioning properly? Are hoses in good condition (not cracked or showing any wear)?
You should be able to answer “yes” to each question. Your initials in each box below the inspection date indicates the device/system was inspected, is operating properly and is compliant with the requirements. On the back of this form, date and describe any actions taken to correct an issue.
This checklist may be used by certified Class A/B Operators to perform weekly inspections at underground storage tank facilities. This checklist, when properly completed, will be accepted by the Maine Department of Environmental Protection as demonstrating compliance with the weekly inspection requirements of 06-096 C.M.R., Chapter 693, Operator Training for Underground Oil and Hazardous Substance Storage Facilities.
| UST-28 |  |  |  |  | REV: November 2017

## 1-Summary
Maine Department of Environmental Protection
Underground Oil Storage Tank
Annual Inspection Report - Summary
Facility Name |  |  |  | Owner | [5 empty] | Registration #
Facility Address |  |  |  | Operator | [5 empty] | Owner Phone
Tank / Chamber #
Volume
Product
Pump Type
|  | Pass | Fail |  | Pass | Fail |  | Pass | Fail |  | Pass | Fail
Class A/B Operator |  |  | 0
Groundwater Monitoring
Interstitial Monitoring
Line Leak Detectors
Heating Oil Tank Piping |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Overfill Prevention
Spill Buckets
Stage I Vapor Recovery
Vent Pipe
Emerg. Elec. Disconnect
Dispenser Area
Cathodic Protection |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Temp. Out-of-Service
Tank and Piping Secondary Testing |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Any FAIL in the columns above means a FAIL for that tank (and the facility). |  | Pass | Fail |  | Pass | Fail |  | Pass | Fail |  | Pass | Fail
By my signature below, I certify that I inspected this facility on this date and found deficiencies that require corrective action(s) before this inspection can be complete and passing.
Printed Name & CTI No. |  |  |  |  | Date |  |  | Incomplete / Failing Inspection Signature
By my signature below, I certify that I inspected this facility on this date and any deficiencies discovered during the inspection have been corrected.
Printed Name & CTI No. |  |  |  |  | Date |  |  | Passing Inspection Signature
The facility owner must submit a passing UST Inspection report to MeDEP within thirty (30) days after the inspection is completed to: | [5 empty] | UST Inspections, Maine Department of Environmental Protection, 17 SHS, Augusta, ME 04333-0017
UST-01 | OWNER MUST KEEP A COPY OF THIS COMPLETED FORM | [9 empty] | Rev Date: | 2023-11-01

## 2-Class AB-Generator
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [6 empty] | AI Date: | 0
Class A/B/C operators are for motor-fuel, waste oil, and marketing & distribution facilities only
Class A/B/C Operators
Item |  |  |  |  | Pass | Fail | Items 2&3 will not affect the "pass/fail" status of this inspection report.
1 | Is a Class A/B Operator employed at this facility?
Certificate # |  | Expires: |  | Name:
[5 empty] | Yes | No
2 | Class A/B Operator documenting the Weekly Walk-through Inspections on a checklist? | [7 empty] | Checklist provided
3 | Class C Operator Training Records on-hand?
Generator Tank
Item |  |  |  |  | Yes | No
4 | Is a UST connected to or fueling a generator?
Emergency Generator
This section is for facilities that have a backup generator that powers the fuel dispensers during a power outage. The emergency generator may or may not be fueled by a UST.
Item |  |  |  |  | Yes | No
5 | Does the facility have an emergency generator that will power dispensers?
6 | What is the fuel capacity of the generator? |  |  |  |  | Gallons
Propane
Diesel
Regular Unleaded
7 | What fuel does the generator use?
Comments: (Indicate all repairs made to bring facility into compliance)
Use this area for additional comments that won't fit on any other pages. Include the Inspection Item #.
UST-01 |  |  | 2 |  |  |  |  | Revision Date: | 2023-11-01

## 3-SW Tanks
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [9 empty] | AI Date: | 0
Single-Walled Tanks Leak Detection
Ground Water Monitoring
(Only for heating oil tanks installed before September 16, 1991)
|  |  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
8 | Monitoring wells accessible?
9 | Monitoring wells marked & secured?
10 | Bailer present, functional and clean?
11 | Water in well?
12 | No floating oil or smell of oil?
13 | Log of weekly well inspection?
PASS or FAIL?
Comments: (Indicate all repairs made to bring facility into compliance)
Use this area for additional comments that won't fit on any other pages. Include the Inspection Item #.
UST-01 |  |  |  |  | 3 |  |  |  |  | Revision Date: | 2023-11-01

## 4-IntrstlMon
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [13 empty] | AI Date: |  | 0
Interstitial Monitoring (Double-walled Tanks and/or Piping)
Console Make and Model:
Item |  | Tank/Chamber # | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  | Volume | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  | Product | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  |  | Yes |  | No |  | Yes |  | No |  | Yes |  | No |  | Yes |  | No
14 | Does the tank have a brine filled interstice?
|  |  | TANK |  | PIPE |  | TANK |  | PIPE |  | TANK |  | PIPE |  | TANK |  | PIPE
15 | Electronic (E), Manual (M), or None (X)
| Manual |  | P | F | P | F | P | F | P | F | P | F | P |  | P | F | P | F
16 | Sump is accessible for inspections?
17 | Written log of sump checks maintained?
| Electronic |  | P | F | P | F | P | F | P | F | P | F | P | F | P | F | P | F
18 | Console is properly programmed and fully operational?
19 | Sensors are properly placed?
20 | All sensors are functioning properly?
| All Systems |  | P | F | P | F | P | F | P | F | P | F | P | F | P | F | P | F
21 | Sumps in liquid tight condition?
22 | No oil in sumps or interstitial space?
23 | No water in sumps or interstitial space?
|  |  | P | F | P | F | P | F | P | F | P | F | P | F | P | F | P | F
PASS or FAIL?
This row is meant to be hidden
Comments: (Indicate all repairs made to bring facility into compliance.)
UST-01 | [5 empty] | 4 | [8 empty] | Revision Date: | 2023-11-01
UST-01 | [7 empty] | 4 | [6 empty] | Revision Date: | 2023-11-01

## 5-LLD¦HO Piping
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [7 empty] | AI Date: | 0
Line Leak Detector (LLD)
Line leak detectors are required on product lines supplied by a pump remote from the dispenser.
Item |  | Tank/Chamber # | 0 |  | 0 |  | 0 |  |  | 0
| Pump Type |  | 0 |  | 0 |  | 0 |  |  | 0
24 | Make and Model (or N/A)
25 | Mechanical (M) or Electronic (E) LLD?
| Mechanical LLD’s only |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
26 | Slow flow when 3 gph leak @ 10 PSI is simulated?
Electronic LLD’s only
27 | System alarms and/or shuts off turbine when a 3 gph leak @ 10 psi is simulated?
PASS or FAIL?
Copper Piping on Heating Oil Tanks
Item |  | Tank/Chamber # | 0 |  | 0 |  | 0 |  |  | 0
|  | Product | 0 |  | 0 |  | 0 |  |  | 0
|  |  | YES | NO | YES | NO | YES | NO |  | YES | NO
28 | Copper Piping?
29 | Piping sleeved or secondarily contained? (* See note below)
30 | Copper suction/return lines in single sleeve separated by spacers?
|  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
PASS or FAIL?
* Heating oil piping installed prior to Sept. 16, 1991 must be sleeved. After that date, piping must be secondarily contained and continuously electronically monitored.
Comments: (Indicate all repairs made to bring facility into compliance.)
UST-01 |  |  |  | 5 |  |  |  |  | Revision Date: | 2023-11-01

## 6-Ovrfll¦Bucket
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [8 empty] | AI Date: | 0
Overfill Prevention |  |  | (Devices must be compatible with fuel delivery method)
|  |  | Tank/Chamber # | 0 |  | 0 |  | 0 |  |  | 0
Item |  | Pump Type |  | 0 |  | 0 |  | 0 |  |  | 0
31 | Ball float (BF), Flapper (F), Pressurized Delivery Flapper (PDF), Electronic (E), Vent Whistle (W), None (X)
|  |  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
32 | Checked and working properly?
33 | Set at 95% of tank capacity? (Auto shut-off / flappers only)
34 | Set at 90% of tank capacity? (Ball floats, electronic & vent whistles)
35 | Vent whistle clearly audible from fill area? (Consumptive use heating oil only)
PASS or FAIL?
Spill Buckets (complete for all spill buckets installed)
|  |  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
36 | Lid in good condition?
37 | Lid not touching fill cap?
38 | Clean?
39 | Liquid tight?
40 | Fill cap and gasket in good condition?
41 | Drop tube? (gasoline/manual stick tanks)
42 | Ends within 6 inches of tank bottom? (gasoline)
PASS or FAIL?
Double-Walled Spill Buckets
|  |  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
43 | Gauge indicator visible?
44 | Floats are properly placed?
45 | All floats are functioning properly?
46 | Interstitial space in liquid tight condition?
PASS or FAIL?
Comments: (Indicate all repairs made to bring facility into compliance.)
UST-01 |  |  |  |  | 6 |  |  |  |  | Revision Date: | 2023-11-01

## 7-VR¦Vent
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [7 empty] | AI Date: | 0
Stage 1 Vapor Recovery
47 | Two-Point (2), Manifold (M), Coaxial (C)
| Two-Point / Manifold |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
48 | Access lid in good condition?
49 | Poppet cap & gasket in good condition?
50 | Poppet valve moves well & closes tight?
Coaxial
51 | Coaxial drop tube in good condition?
PASS or FAIL?
Vent Pipes
| Tank/Chamber # |  | 0 |  | 0 |  | 0 |  |  | 0
Item | Product |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
52 | Vent pipes at least 12 feet above ground level? (Class I)
53 | Vents have proper vent caps?
54 | Vent pipe solidly supported and vertical?
55 | Vent pipe outlets positioned such that vapors will not pose a hazardous condition
PASS or FAIL?
Comments: (Indicate all repairs made to bring facility into compliance.)
UST-01 |  |  |  | 7 |  |  |  |  | Revision Date: | 2023-11-01

## 8-Disprs
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | [15 empty] | AI Date: |  | 0
56 | Emergency Electrical Disconnect properly labeled and accessible? | [5 empty] | Pass |  |  | Fail
57 | Big Red Button immediately accessible to attendant? | [5 empty] | Pass |  |  | Fail |  |  | N/A |  |  | Required only if tank or piping was installed after April 28, 2004
Dispenser Area
Item |  | Dispenser #
| All Systems |  | P | F | P | F |  | P | F |  | P | F |  | P | F | P | F |  | P | F
58 | No weeps or leaks in dispenser?
| Crash Valves |  | P | F | P | F |  | P | F |  | P | F |  | P | F | P | F |  | P | F
59 | Crash valves at correct height?
60 | Crash valves are properly secured?
61 | Crash valves operational?
| Dispenser Sumps |  | P | F | P | F |  | P | F |  | P | F |  | P | F | P | F |  | P | F
62 | Are sumps in liquid tight condition?
63 | No oil in sumps?
64 | No water in sumps?
This row is meant to be hidden
| Electronic Dispenser Sump Monitoring |  | P | F | P | F |  | P | F |  | P | F |  | P | F | P | F |  | P | F
65 | Sensors are properly placed?
66 | All sensors are functioning properly?
|  |  | P | F | P | F |  | P | F |  | P | F |  | P | F | P | F |  | P | F
PASS or FAIL?
This row is meant to be hidden
NOTES: 1) If there are more than seven (7) dispensers, please use additional “Dispenser Area” forms.
2) Since dispensers are not associated with tanks, any FAIL on this page is only recorded in the first tank column on the Summary page. So, if all dispensers are a PASS, only "X" the one dispenser PASS box in the first column of the summary page.
Comments: (Indicate all repairs made to bring facility into compliance.)
Comments: (Indicate all repairs made to bring facility into compliance.)
[9 empty] | 8 | [7 empty] | Revision Date: |  | 2023-11-01

## 9-CP
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [16 empty] | AI Date: |  | 0
Cathodic Protection
Galvanic Systems
Item |  | Tank # | 0 |  |  |  | #REF! | 0 |  |  |  | #REF! | 0 |  |  |  | #REF! | 0 |  |  |  | #REF!
67 | Double-Walled Tanks (one reading taken at tank mid-point)
68 | Single-Walled Tanks (3 readings taken over tank center line)
A "Pass" requires all readings be at least -0.85V |  |  | Pass |  | Fail |  |  | Pass |  | Fail |  |  | Pass |  | Fail |  |  | Pass |  | Fail
This row is meant to be hidden |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE
PASS or FAIL?
This row is meant to be hidden | [5 empty] | #REF! |  |  |  |  | #REF! |  |  |  |  | #REF! |  |  |  |  | #REF!
Impressed Current Systems
|  | Tank # | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Item |  |  | Pass |  | Fail |  |  | Pass |  | Fail |  |  | Pass |  | Fail |  |  | Pass |  | Fail
69 | System met test requirements of NACE TM 101-2012?
70 | Monthly log present and filled out properly?
PASS or FAIL?
This row is meant to be hidden |  |  |  |  | #REF! |  |  |  |  | #REF! |  |  |  |  | #REF! |  |  |  |  | #REF!
By my signature below, I certify that I tested the cathodic protection in accordance with nationally accepted standards. I also certify that I am a properly certified Maine underground oil storage tank installer OR that I am a properly certified Maine underground oil storage tank inspector that has also been certified by the Board of Underground Storage Tank Installers as a cathodic protection tester.
Name & CTI # (Please print) | [7 empty] | Date |  |  |  |  | Signature
Comments: (Indicate all repairs made to bring cathodic protection into compliance.)
UST-01 | [7 empty] | 9 | [10 empty] | Revision Date: | 2023-11-01

## 10-OOS
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [7 empty] | AI Date: | 0
Temporarily Out of Service (OOS) Tanks
Fill out this section for any tank that is neither receiving nor dispensing oil and has been or is intended to be out of service for a period exceeding three months. Prior to returning to service, facilities must submit a complete and passing annual inspection of all facility components. Facilities that have been out of service for more than 12 months without receiving the Department’s permission in writing are required to be properly closed.
Item |  | Tank # | 0 |  | 0 |  | 0 |  |  | 0
|  | Volume | 0 |  | 0 |  | 0 |  |  | 0
|  | Product | 0 |  | 0 |  | 0 |  |  | 0
71 | Date of last dispensing or delivery (Month/Day/Year)
|  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
72-a | Tank pumped out? (Less than 1’’ product, water, and/or residual)
OR
72-b | Electronic Monitoring (tank & piping) is properly operating? (Note: CTI's must complete Line Items 14 & 18-23 for facilities using electronic monitoring in lieu of empting OOS tank(s).
73 | Vent lines open and functioning properly?
74 | All other lines, pumps, manways and ancillary equipment capped and secured?
|  |  | Pass | Fail | Pass | Fail | Pass | Fail |  | Pass | Fail
PASS or FAIL?
Comments: (Indicate all repairs made to bring facility into compliance)
You may use this area for additional comments from previous pages. Include the line item to which it pertains.
UST-01 |  |  | 10 | [5 empty] | Revision Date: | 2023-11-01

## 11-Tank Tightness
Maine Department of Environmental Protection
UST Annual Inspection Report
Reg #: | 0 | [14 empty] | AI Date: |  | 0
Annual Tightness Testing
This section is for tanks that are operating beyond the 30-year warranty and require annual testing beginning in the 35th year. Tanks that are exempt from this requirement are UST's with a brine interstice and piping systems that are single walled safe suction. If a facility is exempt, please submit this form with a comment on what is exempt annually. (This does not apply to consumptive use heating oil tanks.)
Tank Secondary Containment Integrity Testing (dry method)
Item | Tank/Chamber # |  | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  | Volume | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  | Product | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
75 | Tank Material
76 | Test Start Time
77 | Initial Vacuum Reading. Inches Hg
78 | Test Duration |  | 1 hour |  | 2 hours |  |  | 1 hour |  | 2 hours |  | 1 hour |  | 2 hours |  | 1 hour |  | 2 hours
79 | End time
80 | Final Vacuum Reading. Inches Hg.
81 | Is the annular space dry after the test? |  | Yes |  | No |  |  | Yes |  | No |  | Yes |  | No |  | Yes |  | No
| Pass or Fail? |  | P |  | F |  |  | P |  | F |  | P |  | F |  | P |  | F
82 | Test Results Pass or Fail?
Piping Secondary Containment Integrity Testing
| Tank/Chamber # |  | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
|  | Product | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
83 | Piping Material
84 | Test Start Time
85 | Initial Test Pressure, psig
86 | End Test Time
87 | Final Test Pressure, psig
88 | Is there a change in pressure? |  | Yes |  | No |  |  | Yes |  | No |  | Yes |  | No |  | Yes |  | No
| Pass or Fail? |  | P |  | F |  |  | P |  | F |  | P |  | F |  | P |  | F
89 | Test Results Pass or Fail?
This row is meant to be hidden |  |  |  | #REF! |  |  |  |  | #REF! |  |  |  | #REF! |  |  |  | #REF!
Comments: (Indicate all repairs made to bring facility into compliance.)
UST-01 | [5 empty] | 11 | [9 empty] | Revision Date: | 2023-11-01
UST-01 | [8 empty] | 4 | [6 empty] | Revision Date: | 2023-11-01