## CT Calculator
Small Groundwater System
Calculator for
4 Log Inactivation of Viruses
DWP0266
This worksheet will also automatically determine the log-reduction of viruses by your system during peak daily flow based on the following formulas:
| Free Cl (pH 6-9): | Log-reduction = {[CT Actual x e^(0.071 x ((Temp.-32)*(5/9)))] - 0.42} / 2.94
CT Actual = residual (mg/l) x ((volume of storage (gallons) / flow (gpm)) * Baffling Factor)
Enter the Following |  |  | 0.3 Residual | CT is 2.2, 1.3 log reduction. 90% viruses killed
Free Chlorine Residual (mg/l) | 0.9 |  | 0.5 Residual | CT is 3.6, 2.3 log reduction. 99% viruses killed
Water Temperature (Fahrenheit) | 52 |  | 0.83 Residaul | CT is 6.03, 4 log reuction 99.99% viruses killed
Water pH | 7
Peak Flow Rate (gpm) | 9
Lowest Operating Volume (gallon) | 120
Baffle Factor | 0.52
CT Actual (mg-min./l) | 6.24
Log Reduction | 4.5285
Minimum Residual with Safety Factor | 1
Note on B16: Trufant, Christina: Temperature is assumed 50 for all GW systems and___ for all SW systems
Note on B17: If pH is < 6 or > 9, Do not use this formula.
Note on B18: Use the maximum output of well pump