**16 DEPARTMENT OF PUBLIC SAFETY**

**642 BUREAU OF BUILDING CODES AND STANDARDS**

**Chapter 3: MAINE UNIFORM BUILDING AND ENERGY CODE - COMMERCIAL BUILDING CODE OF MAINE**

**SUMMARY:** This chapter establishes the Commercial Building Code component of the Maine Uniform Building and Energy Code “MUBEC.” The provisions of this chapter are based on a nationally recognized model building code published by the International Code Council, Inc., and is made part of the MUBEC through incorporation by reference. This chapter also contains requirements for the enforcement of the Commercial Building code by local building officials in municipalities with a population of more than 4,000 residents.

**SECTION 1. PURPOSE AND SCOPE**

All building construction within a municipality shall be governed by the MUBEC. These codes are adopted by the Technical Building Codes and Standards Board pursuant to 10 M.R.S. Chapter 1103. The primary objective of the Board is to establish a uniform building code throughout the State of Maine.

This chapter sets forth the standards for the construction, alteration, movement, enlargement, replacement, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every building or structure or any appurtenances connected or attached to such building or structure, with the exception of detached one and two-family dwellings and townhouses.

**SECTION 2. AUTHORITY**

The authority for this Chapter is 10 M.R.S. §9722, which provides that the Maine Technical Building Codes and Standards Board shall promulgate rules which adopt, amend, and maintain the Maine Uniform Building and Energy Code. A municipality will have up to 90 days after the effective date of this rule to begin enforcement under the 2015 code.

**SECTION 3. DEFINITIONS**

1. **IBC**. “IBC” means the 2015 International Building Code, published by the International Code Council, Inc.

2. **NFPA**. “NFPA” means The National Fire Protection Association.

3. **MUBEC**. “MUBEC” means the Maine Uniform Building and Energy Code adopted pursuant to 10 M.R.S. §9271 *et seq.*

4. **Technical Building Codes and Standards Board**. “Technical Building Codes and Standards Board” means the board established pursuant to 5 M.R.S. §12004-G, subsection 5-A and 10 M.R.S. §9722.

**SECTION 4. INCORPORATION BY REFERENCE**

1. The following Chapters of the 2015 International Building Code, published by the International Code Council, Inc. are hereby adopted and incorporated by reference:

A. Chapters 1 – 11

B. Chapters 12 – 28

C. Chapters 30 – 33

D. Chapter 35

*E. Appendix C*

2. The following Chapters, and all appendices, of the IBC are specifically excluded from adoption:

A. Chapter 29 PLUMBING SYSTEMS

B. Appendix A*--B, D* --M

**SECTION 5. REVISIONS TO THE IBC**

The following additions, insertions, deletions, and other changes are hereby made to the 2015 International Building Code:

1. Section 101.1

***Delete*** [NAME OF JURISDICTION]; *and*

***Insert*** “State of Maine” in its place.

2. Section 101.4.1

***Delete*** “International Fuel Gas Code”; *and*

***Insert*** “NFPA 54 National Fuel Gas Code: Fire safety codes and standards adopted pursuant to Title 25 M.R.S §§ 2452 and 2465” in its place.

3. Section 101.4.2

***Delete*** Section 101.4.2“Mechanical” in its entirety, without substitution.

4. Section 101.4.3

***Delete*** “International Plumbing Code”; *and*

***Insert*** “Maine State Plumbing Code, adopted pursuant to Title 32, M.R.S §3404-B” in its place.

***Delete*** “International Private Sewage Disposal Codes”; *and*

***Insert*** “Maine State Plumbing Code, adopted pursuant to Title 32, M.R.S §3404-B” in its place.

5. Section 101.4.4

***Delete*** Section 101.4.4 “Property maintenance” in its entirety, without substitution.

6. Section 101.4.5

***Delete*** “International Fire Code”; *and*

***Insert*** “NFPA #1; Fire codes and standards adopted pursuant to Title 25 M.R.S. §§ 2452 and 2465” in its place.

7. Section 102.1

***Insert*** “No provisions of the MUBECshall be construed to prohibit the adoption or enforcement of an ordinance of any political subdivision that sets forth provisions for local enforcement of building codes. Such ordinances may include items such as, permits, permit fees, boards of appeals and violations.”

8. Section 102.4.1

***Delete*** Section 102.4.1

9. Section 102.4.2

***Delete*** section 102.4.2

10. Section 102.6

***Delete*** “International Property Maintenance Code or the International Fire Code”; *and*

***Insert*** “NFPA #1; Fire Safety codes and standards adopted pursuant to Title 25 M.R.S §§ 2452 and 2465” in its place.

11. Section 102.6.2

***Delete*** “International Property Maintenance Code or the International Fire Code”; *and*

***Insert*** “NFPA #1; Fire Safety codes and standards adopted pursuant to Title 25 M.R.S §§ 2452 and 2465” in its place.

12. Section 103

***Delete*** Section 103 “Department of Building Safety” in its entirety, without substitution.

13. Sections 104, 105, 106, 107, 108, 110, 111, 112, 115 and 116 and any amendments thereto shall only be applicable:

A. In a municipality with a population of 4,000 or more residents, beginning:

(1) No later than December 1, 2010, if the municipality had previously adopted any building code on or before August 1, 2008; or

(2) No later than July 1, 2012, if the municipality had not adopted any building code on or before August 1, 2008.

B. In a municipality with a population of less than 4,000 residents if the municipality voluntarily elects to enforce the MUBEC or MUBC.

14. Section 104.8

***Delete*** all language in Section 104.8; *and*

***Insert*** “See 14 MRSA §8101” in its place.

15. Section 105.1

***Insert*** “where required by municipal ordinance” at the end of the paragraph.

16. Section 105.2

***Insert*** “Structures exempt from permits shall be located in compliance with zoning and floodplain regulations” at the end of the paragraph.

17. Section 109

***Delete*** Section 109 “Fees” in its entirety, without substitution.

18. Sections 113 and 114

***Delete*** Section 113 “Board of Appeals” and Section 114 “Violations” in their entirety, without substitution.

19. Section 308.3.3

***Delete*** All language in section 308.3.3; *and*

***Insert*** “See NFPA 101 2015 edition chapter 16”

20. Section 308.6

***Delete*** All language in section 308.6; *and*

***Insert*** “See NFPA 101 2015 edition Chapter 16”

21. Section 308.6.1

***Delete*** “A child day care facility that provides care for more than five but not more than

100 children 2 ½ years or less of age” *and*

***Insert*** “A child day care facility that provides care for more than twelve but not more than 100 children 2 ½ years or less of age.”

22. Section 308.5.2

***Delete*** Section 308.5.2 and the exceptions thereto, in its entirety, without substitution.

23. Section 404.6

***Delete*** all language in Section 404.6; *and*

***Insert*** “See NFPA 101 8.6.7 (2015 edition)” in its place.

24. Section 419.5

***Delete*** this section: “and an automatic sprinkler system in accordance with Section 903.2.8”

25. *Section 602.1.2*

*602.1.2 Alternative Provisions. As an alternative to the construction types defined in 602.2 through 602.5, buildings and structures erected or to be erected, altered or extended in height or area may be classified as construction type IV-A, IV-B or IV-C in accordance with Chapter 6 of the 2021 International Building Code. Buildings and structures classified as IV-A, IV-B or IV-C shall comply with all provisions of the 2021 International Building Code specific to mass timber and the construction type of the building or structure, as well as all other applicable provisions of this code, including provisions for buildings of Type IV construction.*

26. Section 716.5.9.1.2

***Insert*** a new Section 716.5.9.1.2 to read: “Every door assembly in a stair enclosure serving more than four (4) stories shall permit re-entry from the enclosure to the interior of the building. **Exception:** An automatic release that is actuated with the initiation of the building fire alarm or fire detection system shall be provided to unlock all stair enclosure door assemblies to allow re-entry.”

27. Section 717.5.3

***Delete*** “and smoke” in the first sentence.

28. Section 903.2.1.2

***Delete*** “100” and ***Insert*** “300”

*29. Section 903.2.8*

***Insert*** *Exception: An automatic sprinkler system shall not be required in Group R-2 and R-3 occupancies if all of the following conditions are met:*

*1. Building area shall be limited to 600 square feet*

*2. Occupancy is limited to 12 occupants or less*

*3. All sleeping areas shall be located on the ground floor*

*4. All sleeping areas shall have a minimum of one exit directly at grade as well*

*as one additional compliant means of escape*

*5. Equipment requiring fuel combustion, including, but not limited to, heating*

*and cooking equipment, shall not be allowed*

*6. Sleeping area shall not be part of a mixed occupancy*

*7. Buildings of this type shall be located at least 10 feet away from the nearest*

*structure or building governed by this code*

30. Section 903.3.1

***Insert***“and any other adopted standard of the Office of the State Fire Marshal and in accordance with the sprinkler rules in the Office of The State Fire Marshal fire sprinkler technical policy”

31. Section 1004.1.2, Exception

***Delete*** “**Exception:** Where approved by the building official, the actual number of occupants for whom each occupied space, floor or building is designed, although less than those determined by calculation, shall be permitted to be used in the determination of the design occupant load.”

32. Section 1005.1

***Insert*** (within the paragraph; after) The means of egress width shall not be less than required by this section. The total width of means of egress in inches (mm) shall not be less than the total occupant load served by the means of egress multiplied by 0.3 inches (7.61mm) per occupant for stairways.

**Exception**: Board and Care 0.4; Health Care – Sprinkled 0.3; Health Care Non-sprinkled 0.6.

***Delete*** “and by 0.2 inches (5.08 mm) per occupant for other egress components”

***Insert*** The total width of means of egress in inches (mm) shall not be less than the total occupant load served by the means of egress multiplied by 0.2 inches (5.08 mm) per occupant for other egress components.

**Exception**: Board and Care 0.2; Health Care Sprinkled 0.2; Health Care Non-Sprinkled 0.5.

33. Section 1010.1.9.9

***Delete*** “E” from the Group reference in two (2) locations in the first paragraph.

34. Section 1017

***Delete*** all language in Section 1017**;** *and*

***Insert*** “See NFPA 101-2009 Table A7.6” in its place.

35. Section 1017**,** Table 1017.2

***Insert*** “I-1” in the occupancy column as a new row; *and*

***Insert*** “See NFPA 101-2009 Table A7.6”

36. Section 1017, Table 1017.2

***Delete*** “E” from the occupancy column as one of the use groups; *and*

***Insert*** a new row in the column titled “Single Use”; *and*

***Insert*** “E” in the Single Use occupancy column; *and*

***Insert*** “150” in the without sprinkler system (feet) column; *and*

***Insert*** “200” in the sprinkling system (feet) column.

37. Section 1017, Table 1017.2

***Delete*** “S-1 and S-2” from the occupancy column; *and*

***Insert*** “S-1 and S-2” in the occupancy column as a new row; *and*

***Insert*** “See NFPA 101-2009 Table A7.6”

38. Section 1030.5.1

***Insert*** “the means of escape shall be continuously maintained free of all obstructions or impediments to full use in case of fire or other emergency”

39. Section 2801.1

[M] 2801.1 Scope. Mechanical appliances, equipment and systems shall be constructed, installed and maintained in accordance *and*

***Delete*** “with the International Mechanical Code and the International Fuel Gas Code. Masonry chimneys, fireplaces and barbecues shall comply with the International Mechanical Code and Chapter 21 of this code.” *and*

***Insert*** “with ASHRAE 62.1 2016 edition”

STATUTORY AUTHORITY:

10 M.R.S. §9722

EFFECTIVE DATE:

October 11, 2010 – filing 2010-468

AMENDED:

January 23, 2018 – filing 2018-008

November 14, 2021 – filing 2021-227