**Application for a Permit for**

**Aboveground Storage of**

**Flammable and Combustible Liquids**

**Maine Department of Public Safety**

**Office of the State Fire Marshal**

**52 State House Station**

**Augusta, Maine 04333-0052**

**207 626-3880 (Tel.)**

**207 287-6251 (Fax)**

**http://www.maine.gov/dps/fmo/home**

**STOP!** Do Not purchase a tank or start any site work until the permit has been approved!

Don’t pay for work you will have to pay to undo when the permit is denied.

Go to: <https://www.maine.gov/dps/fmo/plans-review/aboveground>for guidelines to the installation of aboveground storage tanks.

Tanks for heating oil that are connected to oil burners and tanks for propane or natural gas are regulated by the Maine Fuel Board

(207) 624-8606.

Underground piping associated with aboveground oil storage tanks is regulated by the Maine Department of Environmental Protection (DEP)

(207) 287-7688. Underground piping must be installed by a DEP Certified Installer. All underground piping associated with motor fuel tanks must be registered with the DEP.

A permit is not required for a tank that is part of a listed generator unit. The unit must be installed according to the manufacturer’s requirements. The capacity of a generator tank is counted for purposes of a Spill Prevention Control and Countermeasures Plan (SPCC).

A permit is not required for a tank that will be on site no more than 180 days, total. The tank must be installed in compliance with all codes and standards, and the manufacturer’s requirements. Maine Department of Environmental Protection Siting Approval is required for a tank that will be on a site for 4 months or more. Contact DEP Directly at (207) 287-7688 if you have a tank that requires DEP Siting Approval, but not a Fire Marshal’s Office permit.

A permit from the Office of the State Fire Marshal is required for any tank with a capacity greater than 60 gallons and for Hydrogen storage tanks. Smaller tanks may require a permit in special situations. A DEP registration does not meet this requirement!

**APPLICATION PROCESS:**

COMPLETE and SUBMIT the application, fee and **digital plans and**

**specifications.** Keep a copy for your records!

The fee is $15 per facility. Make check payable to “Treasurer, State

of Maine”. Include facility name in the note line on the check.

**Do Not Submit Instructions Pages!**

Submit the application, check, **PDF digital drawings and specifications**

for the project by mail. **CD or thumb drive** for the drawings and specs

are the acceptable format. **We are no longer accepting paper drawings**.

Submit a separate set of specification and plan sheets for each

tank on the application. [Page \_\_\_ of \_\_\_ Set \_\_\_ of \_\_\_]

Answer ALL questions! Leaving questions blank will delay

processing of the application. Call (207) 626-3890 if you have a

question about a specific item on the application.

Submit the “Site Plan” and “Side and End View Plan” that will be

used for construction of the facility. Plans must show the facility

details clearly and must include distances listed. Items must be

conspicuously and legibly labeled. Plans for other uses (e.g.,

municipal permits, zoning, drainage, etc.) are NOT acceptable as they

do not show what is needed for this application purpose and much of

the information on other types of plans obscures what is needed to

process the application.

Submit photographs of the tank(s) (side and end views), labels,

appurtenances, and piping if the tanks are available to be photographed.

If this is a change of an existing permit, **submit a copy of the existing permit(s)** marked with the changes. Contact the Office of the State Fire Marshal (207) 626-3890 to determine if there is an existing permit, or to obtain a copy of an existing permit.

**ENGINEER’S CERTIFICATION**

Plans and specifications must be certified by a Maine registered Professional Engineer when the facility will have a total aggregate capacity of 1320 gallons or more.

**DEP SITING REVIEW**

The Fire Marshal’s Office will forward the application to Maine DEP for siting approval. DEP may refuse a permit for a violation of DEP siting rules. You must work directly with DEP if there is a problem with the DEP siting approval.

**DEP REGISTRATION**

Include DEP Registration Information for the facility even when the DEP Registration is for underground tanks or underground piping. This will help DEP determine if the site complies with DEP Siting Rules.

**SPILL PREVENTION CONTROL AND COUNTERMEASURES (SPCC) PLAN**

Federal Environmental Protection Agency (EPA) and DEP require a facility has a SPCC when the facility has an aggregate capacity of 1320 gallons or more. Contact EPA or DEP for more information.

**APPLICATION REVIEW**

The Fire Marshal’s Office will conduct a preliminary review of the application. The applicant shown on the application will be contacted if additional information or clarification of information is required.

You are NOT PERMITTED to construct or operate the facility if the permit is DENIED. When the permit is issued, it will be sent to the owner listed on the application.

**CHANGES TO APPLICATION, PLANS, SPECIFICATIONS, AND FACILITIES**

Any changes to the plans and specifications submitted with this application must be approved by the Office of the State Fire Marshal prior to their implementation and a copy of the changes to the plans must be submitted when the original plans and specifications are changed.

Changing the plans without prior written approval of the Office of the State Fire Marshal voids a permit issued for a facility.

**CANOPIES, ROOFS, AND STORAGE TANK BUILDINGS**

Include plans with dimensions for any building or structures associated with the facility including canopies, roofs, and enclosures.

There are specific requirements for a building or structure to house or protect an aboveground storage tank in NFPA 30 Chapter 24.

Constructing a building or structure not included on the application will void the permit issued based on the application submitted.

A storage tank building is defined as a structure that encloses more than 50% of the total wall space (including dike walls) surrounding the tanks.

A roof must be no less than 3 feet above the top of the tank, and the vent must terminate above the roof.

**PERMIT BY RULE, AGGREGATE INDUSTRY TANKS**

Application for a permit issued under the Permit by Rule program established pursuant to HP 206-LD 253 must be made on an application specific to that program. A permit for a facility that varies in any way from the Permit by Rule process must be made on this application.

**LEGAL**

Requirements for aboveground storage of flammable and combustible liquids are in Title 25 MRSA §2481, et seq., 16-219 CMR Chapter 34 *Rules and Regulations for Flammable and Combustible Liquids*, NFPA 30 *Flammable and Combustible Liquids Code*, NFPA 30-A *Code for Motor Fuel Dispensing Facilities and Repair Garages*, NFPA 385 *Standard for Tank Vehicles for Flammable and Combustible Liquids* and *NFPA 409 Standard for Aircraft Fuel Servicing*.

**HAZARD IDENTIFICATION**

Tanks must be marked “No Smoking.

Tanks must be marked with the name of the product.

Tanks must be marked with the NFPA 704 Hazard Identification System shown below. Show the numbers on the application that are appropriate for the product in your tank. These numbers are available from your supplier and from the Material Safety Sheet for the products.

Do not use a DOT transportation placard!



|  |  |  |
| --- | --- | --- |
| State Seal (color)  **Application for a Permit for**  **Aboveground Storage of**  **Flammable and Combustible Liquids**  **Maine Department of Public Safety**  **Office of the State Fire Marshal**  **52 State House Station**  **Augusta, Maine 04333-0052**  **207 626-3880 (Tel.)**  **207 287-6251 (Fax)**  **http://www.maine.gov/dps/fmo/home** | **FMO Use Only** | |
| DEP Siting:  Complies  Exempt  Does Not Comply  May Be Made To  Comply  Waiver  Requested  Waiver Granted | Permit #  \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  Issued:  \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ |
| Action:  Approved  per Plan  Approved per  Plan and  Inspection  Denied    \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  By: \_\_\_\_\_\_\_\_\_\_\_    Date: \_\_\_\_\_\_\_\_\_ |
| Fee:  Amount: $\_\_\_\_\_\_\_\_  Received: \_\_\_\_\_\_\_  Check #: \_\_\_\_\_\_\_\_ |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **FACILITY:** | | | | |
| Facility Name: | | | | |
| Facility Physical Address: | | | | |
| Facility City: | | Facility County: | | Facility Zip Code: |
| Facility Telephone: | | | | |
| Facility Contact Person: | Facility Contact Telephone: | | Facility Contact Email: | |
| Total Capacity of Facility:        U. S. Gallons | Fire Marshal’s Office Permit: None  Number:       Issued:  **Attach a copy to this application!** | | | |
| Facility DEP Registration Number: | DEP Registration Date: | | | |
| Owner Start Date: | Operator Start Date: | | | |
|  | | | | |

|  |
| --- |
| **DEP USE OF FACILITY:** |
| |  |  |  | | --- | --- | --- | | Wholesale Oil  Retail Oil  Public Facilities  Private Fueling | Industrial  Aggregate Mining  Chemical Storage  Multiple Residence  Single Residence | Federal Facility  State Facility  Town or School Facility | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **APPLICANT: (Person submitting application and who should be contacted for additional information)** | | | | |
| Name: | | | | |
| Mailing Address: | City: | | State: | Zip Code: |
| Physical Address: | City: | | State: | Zip Code: |
| Telephone, including extension: | | Email: | | |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

|  |
| --- |
| **ENGINEER’S CERTIFICATION:** |
| **Plans and specifications must be certified by a Maine registered Professional Engineer when the total capacity of the facility is**  **1320 gallons or more.** |
| I,      \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ hereby certify that  (Name, typed or printed)  the facility described on this application is designed according  to recognized engineering practices, industry standards, statutes,  rules, codes, and standards.  \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  (Signature)       \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  (Engineer’s Company)       \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  (Engineer’s Telephone, including extension)       \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_  (Engineer’s Email) Engineer’s Seal |

|  |
| --- |
| **TYPE OF PERMIT:** |
| New Aboveground Storage Facility **(No existing permit)**  Change of facility **(Attach a copy of existing permit)**  Add tank(s)  Replace tank(s)  Remove tank(s)  Change Product(s)  Change of Ownership **(Attach a copy of existing permit)**  Note changes and corrections to a copy of the existing permit, and submit the corrected  copy of the existing permit with the application.  Corrections to Permit **(Attach a copy of existing permit)**  Note changes and corrections to a copy of the existing permit and submit the corrected  copy of the existing permit with the application. |

|  |  |  |  |
| --- | --- | --- | --- |
| **FACILITY OWNER:** | | | |
| Name: | | | |
| Mailing Address: | City: | State: | Zip Code: |
| Physical Address: | City: | State: | Zip Code: |
| Contact: | Telephone: | Email: | |
| Yes No Is this a new owner? | | | |
| Permit will be mailed to “Facility Owner” as shown above. | | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **FACILITY OPERATOR:**  Same as Facility Owner | | | |
| Name: | | | |
| Mailing Address: | City: | State: | Zip Code: |
| Physical Address: | City: | State: | Zip Code: |
| Contact: | Telephone: | Email: | |
| Yes No Is this a new operator? | | | |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

Copy these pages as needed for additional tanks.

Page 1 of 4, Set \_\_\_\_\_ of \_\_\_\_\_

|  |  |  |
| --- | --- | --- |
| **TANK INFORMATION:** | | |
| Tank Number: (Consecutive Numbers starting at 1) | Facility Tank Number, if different from Tank Number: | |
| Nominal Capacity of tank:        US Gallons | Tank Manufacturer: | |
| Tank Material:  Steel Other (Specify): | | Tank Orientation:  Horizontal Vertical |
| Listing:  UL 80 UL 2080 Protected Tank  UL 142 (for Storage only, No Fleet Dispensing) UL 2085 Fire Resistant Tank  UL 142 With Factory Installed Dispenser  UL 142 with Secondary Containment UL 2245 Tank in a Vault  Other (Specify): | | |
| **Use of Tank:**  Public Fueling/Fleet Fueling  Automotive Aviation Marina Equipment Other:  Private Personal Fueling  Automotive Aviation Marina Equipment Other:  Bulk Storage  Equipment Supply (Specify):  Container Storage  Other (Specify): | | |
| **Flood Zone:** Is the tank in a Flood Zone? If “Yes”, specify what means will be used to secure  **Yes** **No** the tank against moving: | | |
| **Vault:** Is the tank in a vault? (A concrete secondary containment dike is NOT a vault.)  **Yes No** If the vault is listed, specify the listing: | | |
| **Secondary Containment:**  Dike, Concrete Double Wall Tank  Dike, Metal Remote Impoundment  Dike, Earth None | | |
| **Weather Protection:**  Inside a building **Submit plans and specifications for the building with this application!**  (More than 50% of wall space is enclosed. Building must comply with NFPA 30, Chapter 24,  NAPA 1, NFPA 101, and other referenced publications)  Roof with walls (Less than 50% of the total wall space, including dike walls, is enclosed.)  Roof or Canopy Only  None | | |
| **Security:**  Chain Link Fence Enclosure Fence is no less than 6 feet high, 10 feet from tank.  Entire property is fenced  Other (Specify): | | |
| **Collision Protection:**  Barricades  Bollards  Other (Specify): | | |
| **Distances:**  Distance of tank from:  Nearest Important Building      ft Dispensers      ft  Nearest Property Line      ft Public Fueling Minimum 50 feet  Nearest side of a Public Way      ft Private Fueling  Other Tanks Minimum 3 feet      ft Mounted on tank (UL2080/2085 Only)  Propane Storage Minimum 20 feet      ft | | |
| **Electrical Wiring and Equipment:**  Yes No None Are electrical wiring and electrical equipment within the hazard area  defined by the National Electrical Code, NFPA 70 and NFPA 30, installed in  compliance with these codes? | | |
| **Tank Leak Detection:**  None Electronic/Ground Water Manual Monitoring/Secondary  Automatic Tank Gauge Electronic/Vapor Containment  Electronic/Secondary Containment Statistical Inventory Analysis Manual Groundwater Sampling  Other (specify): | | |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

Copy these pages as needed for additional tanks or chambers.

Page 2 of 4, Set \_\_\_\_\_ of \_\_\_\_\_

|  |  |  |  |
| --- | --- | --- | --- |
| **CHAMBER INFORMATION** | Chamber 1 | Chamber 2 | Chamber 3 |
| Capacity (US Gallons) |  |  |  |
| Product  Use generic name, not trade name. | Alcohol  Antifreeze  Asphalt  Biodiesel B1-B74  Biodiesel B75-B99  Biodiesel B100  Crude Oil  Diesel Fuel  #2 Fuel  Gasoline,  Aviation  Gasoline, E-85  Gasoline, Leaded  Gasoline, Plus  Gasoline, Premium  Gasoline, Regular  Glycerol  Hydraulic Oil  Jet Fuel  Kerosene  Lube Oil  Methanol  Vegetable Oil  Waste Oil  Other (Specify): | Alcohol  Antifreeze  Asphalt  Biodiesel B1-B74  Biodiesel B75-B99  Biodiesel B-100  Crude Oil  Diesel Fuel  #2 Fuel  Gasoline,  Aviation  Gasoline, E-85  Gasoline, Leaded  Gasoline, Plus  Gasoline, Premium  Gasoline, Regular  Glycerol  Hydraulic Oil  Jet Fuel  Kerosene  Lube Oil  Methanol  Vegetable Oil  Waste Oil  Other (Specify): | Alcohol  Antifreeze  Asphalt  Biodiesel B1-B74  Biodiesel B75-B99  Biodiesel B-100  Crude Oil  Diesel Fuel  #2 Fuel  Gasoline,  Aviation  Gasoline, E-85  Gasoline, Leaded  Gasoline, Plus  Gasoline, Premium  Gasoline, Regular  Glycerol  Hydraulic Oil  Jet Fuel  Kerosene  Lube Oil  Methanol  Vegetable Oil  Waste Oil  Other (Specify): |
| Is Product Heated? | Yes No | Yes No | Yes No |
| Is Product Under Pressure? | Yes No | Yes No | Yes No |
| Does fill pipe Terminate within 6” of the bottom of the tank? Mandatory for tanks storing  Class I liquids | Yes No | Yes No | Yes No |
| Does filling slow at 90% and stop at 95% of tank capacity? Mandatory for Secondary Containment Tanks. | Yes No | Yes No | Yes No |
| Overfill Protection | Level Gauge  Vent Whistle  Drop Tube  Electronic  Mechanical  Mech + Elect  None | Level Gauge  Vent Whistle  Drop Tube  Electronic  Mechanical  Mech + Elect  None | Level Gauge  Vent Whistle  Drop Tube  Electronic  Mechanical  Mech + Elect  None |
| Normal Vent (Size & Type) |  |  |  |
| Normal Vent (Height Above Ground)  Class I Liquids No less than 12 feet above ground |  |  |  |
| Emergency Vent for Primary Chamber (Size & Type) |  |  |  |
| Emergency Vent for Interstitial Space (Size & Type) |  |  |  |
| **Marking of Tank:**  Product Name **Mandatory**  “No Smoking” **Mandatory**  NFPA 704 Hazard Identification System  **Mandatory** (See Instructions, Page 3) | Yes No  Blue  Red  Yellow  White | Yes No  Blue  Red  Yellow  White | Yes No  Blue  Red  Yellow  White |
| Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_  Copy these pages as needed for additional tanks or chamberss.  Page 3 of 4, Set \_\_\_\_\_ of \_\_\_\_\_   |  |  |  |  | | --- | --- | --- | --- | | **TYPE OF PUMP (Factory Mounted Only for UL 142 tanks):** | Pressure  Suction  None | Pressure  Suction  None | Pressure  Suction  None | | If pump is a pressure pump, is there pressure relief? | Yes No | Yes No | Yes No | | If pump is a suction pump, is there an anti-siphon device? | Yes No | Yes No | Yes No | | **PIPING MATERIAL:**  Steel Other **(Specify):** | | | | | **UNDERGROUND PIPING:**  Yes No Is any of the piping underground?  If “Yes”, Indicate the type of underground piping below:  Steel, Asphalt Coated Steel, Cathodic Protected  Steel, Secondary Containment Fiberglass, Single Walled  Fiberglass, Secondary Containment, Petro Fiberglass, Petroleum  Fiberglass, Sec Cont, Petro, Alcohol Composite Fiberglass with Bonded Steel  Composite with Cathodic Protection Composite with Secondary Containment  Copper Black Steel  PVC Stainless Steel  Double Wall Cathode Protected Steel Flexible Single Walled Piping  Flexible Double Walled Piping Copper with Secondary Containment | | | | | **PIPING LEAK DETECTION:**  None Manual Monitoring, Secondary Containment  Electronic, Secondary Containment Manual Groundwater Sampling  Electronic, Groundwater Statistical Inventory Analysis  Continuous Electronic Vapor Monitoring | | | | | | | |
|  |
|  | | | |
|  | | | |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

Copy these pages as needed for additional tanks.

Page 4 of 4, Set \_\_\_\_\_ of \_\_\_\_\_

**SIDE AND END VIEWS PLAN**

**(These are the plans to be used to construct the facility!)**

|  |
| --- |
| **Show All of the Following on this Diagram:**  >Base Material >Emergency Vents >Piping >Protection >Buildings and Dimensions  >Ground and Foundation >Primary Chamber >Routing of Piping >Fire Extinguishing >Building Construction Type  >Type of Secondary >Type and Size >Piping Connections >From Flooding >Building Materials  Containment >Interstitial Space >Valves >From Collision >Floor Plan  >Dike >Type and Size >Anti-Siphon >From Tampering >Exit Routes and Exit Signs  >Construction Material >Pressure Relief >Alarm System  >Inside Dimensions >Electrical Equipment >Break-away >Tank Marking >Emergency Lights  >Capacity >Emergency Disconnects >Piping Supports >”No Smoking” >Sprinkler System Specs  >Drain and Valve >Spill Bucket >Product Name >Secondary Containment  >Remote Impounding >Loading Docks >NFPA 704 Placard >Tank Fill and Vent  >Tanks >Vehicle Containment >Color Code  >Tank Supports >Bonding Connection >On Tanks >Roofs and Canopies  >Normal Vents >Self Closing Valves >On Piping >Construction Plans  >Type and Size >Height Above Top of Tank  >Height Above Ground >Vent Termination |
|  |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

**SITE PLAN**

**(This is the plan to be used to construct the facility!)**

|  |  |  |
| --- | --- | --- |
| **Show the Location of All of the Following on this Plan:**  >Tanks and Dikes >Electrical Controls >Loading & Unloading  >Buildings >Emergency Disconnects Piping  >Property Lines >Fire Extinguishing >Sump Leak Detection  >Public Ways Equipment >Remote Impounding  >Dispensers >Security Features >Designated Smoking Area  >Propane Storage >Collision Protection | **Show the Distance from the Tanks to the following on this plan:**  >Buildings >Other Tanks  >Property Lines >Dispensers  >Public Ways >Propane Storage | Indicate  **NORTH**  With Arrow |
|  | | |

Facility: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ City: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Application Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_

|  |
| --- |
| Section A-1  If you answer “Yes” to any of the following questions, your facility is exempt from the siting restrictions.  Yes No  1. Was the tank facility installed before September 30, 2008?  2. Will the facility be used solely to store heating oil that is consumed on site, not  resold?  3. Is the facility replacing an aboveground oil storage facility that was installed  before September 30, 2008 that is on the same property?  4. Is the facility replacing or expanding an underground oil storage facility that was  registered on or before September 30, 2008 and is presently on the same property?  If “Yes” enter the DEP Registration Number:\_\_\_\_\_\_\_\_\_\_\_\_\_\_ |
| Section A-2  If you answered “No” to all the questions in A-1, complete this section.  1. Will any portion of the facility be installed after September 30, 2008?  (If “No”, Section A-2 does not apply to the tank(s) you are installing.)  2. Will any portion of the facility be located within 300 feet of a private well or  water supply?  (This does not include a private well located on the same lot as the facility and  serving only users living on that property.)  3. Will any portion of the facility be located within the source water protection area  of a public drinking water well mapped by the Department of Human Services or  within 1000 feet of a public water well, whichever is greater?  Maps of source water protection areas are available on the internet at  [**www.maine.gov/dhs/eng/water/index.htm**](http://www.maine.gov/dhs/eng/water/index.htm). Public water supplies are defined  as any well or water supply where water is obtained, sold, furnished, or  distributed to the public for human consumption. The well or water supply must  meet one or more of the following requirements to be a public water supply:  • Serves more than 15 connections, OR  • Regularly Serves at least 25 individuals daily for at least 60 days  of the year, OR  • Provides bottled water for sale where the water is pumped from on site. |
| 4. Does the well or water supply serve a school or community water supply  system?  (A school is an institution for the formal classroom instruction of  children in grades k-12. A community water system is a public water  system that serves at least 15 service connections used by year-round  residents or regularly serves at least 25 year-round residents.)  5. Will any portion of the facility be located within a mapped significant sand and  gravel aquifer?  As of July 1, 2010, Maine law prohibits installation of ASTs within significant  sand and gravel aquifers mapped by the Maine Geological Survey unless a variance is  obtained from the Department of Environmental Protection (DEP).  If the answer to #2 or #4 above is “Yes”, a new aboveground oil storage facility may not be installed unless the applicant proves there is no hydrogeologic connection between the proposed facility and the water supply at issue. Contact DEP at (207) 287-7688 to obtain information on the procedures to follow to determine if a hydrogeologic connection exists.  If the answer to #3 is “Yes” and the answer to #4 is “No”, then a variance from the siting restriction may be granted upon written application to DEP if DEP determines that the proposed installation is designed to exceed minimum regulatory requirements and will effectively minimize releases of oil and the likelihood of drinking water contamination.  If the answer to #5 is “YES”, Please review Chapter 692, Section (4)-(B) through (E) to determine if a variance may be applicable for the proposed site. Contact DEP for an application for a variance.  For questions about the siting law, please call (207) 287-7688 or visit the DEP Drinking Water Protection website: www.maine.gov/dep/rwm/drinkingwater/index.htm |
|  |
|  |