Application for a Permit for

Aboveground Storage of

Flammable and Combustible Liquids

Maine Department of Public Safety

Office of the State Fire Marshal

52 State House Station

Augusta, Maine 04333-0052

207 626-3880 (Tel.)

207 287-6251 (Fax)

http ;//www.maine,gov/dps/fmo/index.htm

STOP! Do Not purchase a tank or start any site work until the permit has been approved!

Don’t pay for work you will have to pay to undo when the permit is denied.

Go to: http://www.maine.gov/dps/fmo/plans/storage_tanks.html for guidelines to the installation of aboveground storage tanks.

Tanks for heating oil that are connected to oil burners and tanks for propane or natural gas are regulated by the Maine Fuel Board

(207) 624-8606.

Underground piping associated with aboveground oil storage tanks is regulated by the Maine Department of Environmental Protection (DEP)

(207) 287-7688.  Underground piping must be installed by a DEP Certified Installer.  All underground piping associated with motor fuel tanks must be registered with the DEP.

A permit is not required for a tank that is part of a listed generator unit.  The unit must be installed according to the manufacturer’s requirements.  The capacity of a generator tank is counted for purposes of a Spill Prevention Control and Countermeasures Plan (SPCC).

A permit is not required for a tank that will be on site no more than 180 days, total.  The tank must be installed in compliance with all codes and standards, and the manufacturer’s requirements.  Maine Department of Environmental Protection Siting Approval is required for a tank that will be on a site for 4 months or more.  Contact DEP Directly at (207) 287-7688 if you have a tank that requires DEP Siting Approval, but not a Fire Marshal’s Office permit.

A permit from the Office of the State Fire Marshal is required for any tank with a capacity greater than 60 gallons and for Hydrogen storage tanks. Smaller tanks may require a permit in special situations.  A DEP registration does not meet this requirement!

APPLICATION PROCESS:

COMPLETE and SUBMIT the application and fee.

Keep a copy of the application, plans, and specifications for your record!

The fee is $15 per facility.  Make check payable to “Treasurer, State of Maine”.  Include facility name in the note line on the check.

Do Not Submit Instructions Pages!

Submit the application and check for the fee by mail.

Submit a separate set of specification and plan sheets for each tank on the application. [Page ___ of ___ Set ___ of ___]

Answer ALL questions!  Leaving questions blank will delay processing of the application.  Call (207) 626-3890 if you have a question about a specific item on the application.

Submit the “Site Plan” and “Side and End View Plan” that will be used for construction of the facility. Plans must show the facility details clearly and must include distances listed.  Items must be conspicuously and legibly labeled.  Plans for other uses (e.g., municipal permits, zoning, drainage, etc.) are NOT acceptable as they do not show what is needed for this application purpose and much of the information on other types of plans obscures what is needed to process the application.  Full sized blueprints reduced to 8½” X 11” are NOT ACCEPTABLE because they are too small to be legible.

Submit photographs of the tank(s) (side and end views), labels, appurtenances, and piping if the tanks are available to be photographed.

If this is a change of an existing permit, submit a copy of the existing permit(s) marked with the changes.  Contact the Office of the State Fire Marshal (207) 626-3890 to determine if there is an existing permit, or to obtain a copy of an existing permit.

ENGINEER’S CERTIFICATION

Plans and specifications must be certified by a Maine registered Professional Engineer when the facility will have a total aggregate capacity of 1320 gallons or more.

DEP SITING REVIEW

The Fire Marshal’s Office will forward the application to Maine DEP for siting approval.  DEP may refuse a permit for a violation of DEP siting rules.  You must work directly with DEP if there is a problem with the DEP siting approval.

DEP REGISTRATION

Include DEP Registration Information for the facility even when the DEP Registration is for underground tanks or underground piping.  This will help DEP determine if the site complies with DEP Siting Rules.

SPILL PREVENTION CONTROL AND COUNTERMEASURES (SPCC) PLAN

Federal Environmental Protection Agency (EPA) and DEP require a facility has a SPCC when the facility has an aggregate capacity of 1320 gallons or more.  Contact EPA or DEP for more information.

APPLICATION REVIEW

The Fire Marshal’s Office will conduct a preliminary review of the application.  The applicant shown on the application will be contacted if additional information or clarification of information is required.

You are NOT PERMITTED to construct or operate the facility if the permit is DENIED.  When the permit is issued, it will be sent to the owner listed on the application.

CHANGES TO APPLICATION, PLANS, SPECIFICATIONS, AND FACILITIES

Any changes to the plans and specifications submitted with this application must be approved by the Office of the State Fire Marshal prior to their implementation and a copy of the changes to the plans must be submitted when the original plans and specifications are changed.

Changing the plans without prior written approval of the Office of the State Fire Marshal voids a permit issued for a facility.

CANOPIES, ROOFS, AND STORAGE TANK BUILDINGS

Include plans with dimensions for any building or structures associated with the facility including canopies, roofs, and enclosures.

There are specific requirements for a building or structure to house or protect an aboveground storage tank in NFPA 30 Chapter 24.

Constructing a building or structure not included on the application will void the permit issued based on the application submitted.

A storage tank building is defined as a structure that encloses more than 50% of the total wall space (including dike walls) surrounding the tanks.

A roof must be no less than 3 feet above the top of the tank, and the vent must terminate above the roof.

PERMIT BY RULE, AGGREGATE INDUSTRY TANKS

Application for a permit issued under the Permit by Rule program established pursuant to HP 206-LD 253 must be made on an application specific to that program.  A permit for a facility that varies in any way from the Permit by Rule process must be made on this application.

LEGAL

Requirements for aboveground storage of flammable and combustible liquids are in Title 25 MRSA §2481, et seq., 16-219 CMR Chapter 34 Rules and Regulations for Flammable and Combustible Liquids, NFPA 30 Flammable and Combustible Liquids Code, NFPA 30-A Code for Motor Fuel Dispensing Facilities and Repair Garages, NFPA 385 Standard for Tank Vehicles for Flammable and Combustible Liquids and NFPA 409 Standard for Aircraft Fuel Servicing.

HAZARD IDENTIFICATION

Tanks must be marked “No Smoking.

Tanks must be marked with the name of the product.

Tanks must be marked with the NFPA 704 Hazard Identification System shown below.  Show the numbers on the application that are appropriate for the product in your tank.  These numbers are available from your supplier and from the Material Safety Sheet for the products.

Do not use a DOT transportation placard!

| Application for a Permit for Aboveground Storage of Flammable and Combustible Liquids Maine Department of Public Safety Office of the State Fire Marshal 52 State House Station Augusta, Maine 04333-0052 207 626-3880 (Tel.) 207 287-6251 (Fax) http ;//www.maine,gov/dps/fmo/index.htm | FMO Use Only |  |
| --- | --- | --- |
|  | DEP Siting: Complies Exempt Does Not Comply May Be Made To Comply Waiver Requested Waiver Granted | Permit # ___________________ Issued: ___________________ |
|  |  | Action: Approved per Plan Approved per Plan and Inspection Denied _______________ By: ___________ Date: _________ |
|  | Fee: Amount: $________ Received: _______ Check #: ________ |  |

| FACILITY: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Facility Name: |  |  |  |  |
| Facility Physical Address: |  |  |  |  |
| Facility City: |  | Facility County: |  | Facility Zip Code: |
| Facility Telephone: |  |  |  |  |
| Facility Contact Person: | Facility Contact Telephone: |  | Facility Contact Email: |  |
| Total Capacity of Facility: U. S. Gallons | Fire Marshal’s Office Permit: None Number: Issued: Attach a copy to this application! |  |  |  |
| Facility DEP Registration Number: | DEP Registration Date: |  |  |  |
| Owner Start Date: | Operator Start Date: |  |  |  |

DEP USE OF FACILITY:

Wholesale Oil Retail Oil Public Facilities Private Fueling; Industrial Aggregate Mining Chemical Storage Multiple Residence Single Residence; Federal Facility State Facility Town or School Facility.

| APPLICANT: (Person submitting application and who should be contacted for additional information) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name: |  |  |  |  |
| Mailing Address: | City: |  | State: | Zip Code: |
| Physical Address: | City: |  | State: | Zip Code: |
| Telephone, including extension: |  | Email: |  |  |

Facility: _______________________ City: ________________________ Application Date: ______________

ENGINEER’S CERTIFICATION:

Plans and specifications must be certified by a Maine registered Professional Engineer when the total capacity of the facility is 1320 gallons or more.

I, _______________________________ hereby certify that (Name, typed or printed) the facility described on this application is designed according to recognized engineering practices, industry standards, statutes, rules, codes, and standards. ___________________________________ (Signature) ______________________________ (Engineer’s Company) ______________________________ (Engineer’s Telephone, including extension) ______________________________ (Engineer’s Email) Engineer’s Seal

TYPE OF PERMIT:

New Aboveground Storage Facility (No existing permit) Change of facility (Attach a copy of existing permit) Add tank(s) Replace tank(s) Remove tank(s) Change Product(s) Change of Ownership (Attach a copy of existing permit) Note changes and corrections to a copy of the existing permit, and submit the corrected copy of the existing permit with the application. Corrections to Permit (Attach a copy of existing permit) Note changes and corrections to a copy of the existing permit and submit the corrected copy of the existing permit with the application.

| FACILITY OWNER: |  |  |  |
| --- | --- | --- | --- |
| Name: |  |  |  |
| Mailing Address: | City: | State: | Zip Code: |
| Physical Address: | City: | State: | Zip Code: |
| Contact: | Telephone: | Email: |  |
| Yes No Is this a new owner? |  |  |  |
| Permit will be mailed to “Facility Owner” as shown above. |  |  |  |

| FACILITY OPERATOR: Same as Facility Owner |  |  |  |
| --- | --- | --- | --- |
| Name: |  |  |  |
| Mailing Address: | City: | State: | Zip Code: |
| Physical Address: | City: | State: | Zip Code: |
| Contact: | Telephone: | Email: |  |
| Yes No Is this a new operator? |  |  |  |

Facility: _______________________ City: ________________________ Application Date: ______________

Copy these pages as needed for additional tanks.

Page 1 of 4, Set _____ of _____

| TANK INFORMATION: |  |  |
| --- | --- | --- |
| Tank Number: (Consecutive Numbers starting at 1) | Facility Tank Number, if different from Tank Number: |  |
| Nominal Capacity of tank: US Gallons | Tank Manufacturer: |  |
| Tank Material: Steel Other (Specify): |  | Tank Orientation: Horizontal Vertical |
| Listing: UL 80 UL 2080 Protected Tank UL 142 UL 2085 Fire Resistant Tank UL 142 with Secondary Containment UL 2245 Tank in a Vault Other (Specify): |  |  |
| Use of Tank: Public Fueling Automotive Aviation Marina Equipment Other: Private Fueling Automotive Aviation Marina Equipment Other: Bulk Storage Equipment Supply (Specify): Container Storage Other (Specify): |  |  |
| Flood Zone: Is the tank in a Flood Zone? If “Yes”, specify what means will be used to secure Yes No the tank against moving: |  |  |
| Vault: Is the tank in a vault? (A concrete secondary containment dike is NOT a vault.) Yes No If the vault is listed, specify the listing: |  |  |
| Secondary Containment: Dike, Concrete Double Wall Tank Dike, Metal Remote Impoundment Dike, Earth None |  |  |
| Weather Protection: Inside a building Submit plans and specifications for the building with this application! (More than 50% of wall space is enclosed. Building must comply with NFPA 30, Chapter 24, NAPA 1, NFPA 101, and other referenced publications) Roof with walls (Less than 50% of the total wall space, including dike walls, is enclosed.) Roof or Canopy Only None |  |  |
| Security: Chain Link Fence Enclosure Fence is no less than 6 feet high, 10 feet from tank. Entire property is fenced Other (Specify): |  |  |
| Collision Protection: Barricades Bollards Other (Specify): |  |  |
| Distances: Distance of tank from: Nearest Important Building ft Dispensers ft Nearest Property Line ft Public Fueling Minimum 50 feet Nearest side of a Public Way ft Private Fueling Other Tanks Minimum 3 feet ft Mounted on tank Propane Storage Minimum 20 feet ft |  |  |
| Electrical Wiring and Equipment: Yes No None Are electrical wiring and electrical equipment within the hazard area defined by the National Electrical Code, NFPA 70 and NFPA 30, installed in compliance with these codes? |  |  |
| Tank Leak Detection: None Electronic/Ground Water Manual Monitoring/Secondary Automatic Tank Gauge Electronic/Vapor Containment Electronic/Secondary Containment Statistical Inventory Analysis Manual Groundwater Sampling Other (specify): |  |  |

Facility: _______________________ City: ________________________ Application Date: ______________

Copy these pages as needed for additional tanks or chambers.

Page 2 of 4, Set _____ of _____

| CHAMBER INFORMATION | Chamber 1 | Chamber 2 | Chamber 3 |
| --- | --- | --- | --- |
| Capacity (US Gallons) |  |  |  |
| Product Use generic name, not trade name. | Alcohol Antifreeze Asphalt Biodiesel B1-B74 Biodiesel B75-B99 Biodiesel B100 Crude Oil Diesel Fuel #2 Fuel Gasoline, Aviation Gasoline, E-85 Gasoline, Leaded Gasoline, Plus Gasoline, Premium Gasoline, Regular Glycerol Hydraulic Oil Jet Fuel Kerosene Lube Oil Methanol Vegetable Oil Waste Oil Other (Specify): | Alcohol Antifreeze Asphalt Biodiesel B1-B74 Biodiesel B75-B99 Biodiesel B-100 Crude Oil Diesel Fuel #2 Fuel Gasoline, Aviation Gasoline, E-85 Gasoline, Leaded Gasoline, Plus Gasoline, Premium Gasoline, Regular Glycerol Hydraulic Oil Jet Fuel Kerosene Lube Oil Methanol Vegetable Oil Waste Oil Other (Specify): | Alcohol Antifreeze Asphalt Biodiesel B1-B74 Biodiesel B75-B99 Biodiesel B-100 Crude Oil Diesel Fuel #2 Fuel Gasoline, Aviation Gasoline, E-85 Gasoline, Leaded Gasoline, Plus Gasoline, Premium Gasoline, Regular Glycerol Hydraulic Oil Jet Fuel Kerosene Lube Oil Methanol Vegetable Oil Waste Oil Other (Specify): |
| Is Product Heated? | Yes No | Yes No | Yes No |
| Is Product Under Pressure? | Yes No | Yes No | Yes No |
| Does fill pipe Terminate within 6” of the bottom of the tank? Mandatory for tanks storing Class I liquids | Yes No | Yes No | Yes No |
| Does filling slow at 90% and stop at 95% of tank capacity? Mandatory for Secondary Containment Tanks. | Yes No | Yes No | Yes No |
| Overfill Protection | Level Gauge Vent Whistle Drop Tube Electronic Mechanical Mech + Elect None | Level Gauge Vent Whistle Drop Tube Electronic Mechanical Mech + Elect None | Level Gauge Vent Whistle Drop Tube Electronic Mechanical Mech + Elect None |
| Normal Vent (Size & Type) |  |  |  |
| Normal Vent (Height Above Ground) Class I Liquids No less than 12 feet above ground |  |  |  |
| Emergency Vent for Primary Chamber (Size & Type) |  |  |  |
| Emergency Vent for Interstitial Space (Size & Type) |  |  |  |
| Marking of Tank: Product Name Mandatory “No Smoking” Mandatory NFPA 704 Hazard Identification System Mandatory (See Instructions, Page 3) | Yes No Blue Red Yellow White | Yes No Blue Red Yellow White | Yes No Blue Red Yellow White |
| Facility: _______________________ City: ________________________ Application Date: ______________ Copy these pages as needed for additional tanks or chamberss. Page 3 of 4, Set _____ of _____ TYPE OF PUMP:; Pressure Suction None; Pressure Suction None; Pressure Suction None. If pump is a pressure pump, is there pressure relief?; Yes No; Yes No; Yes No. If pump is a suction pump, is there an anti-siphon device?; Yes No; Yes No; Yes No. PIPING MATERIAL: Steel Other (Specify):. UNDERGROUND PIPING: Yes No Is any of the piping underground? If “Yes”, Indicate the type of underground piping below: Steel, Asphalt Coated Steel, Cathodic Protected Steel, Secondary Containment Fiberglass, Single Walled Fiberglass, Secondary Containment, Petro Fiberglass, Petroleum Fiberglass, Sec Cont, Petro, Alcohol Composite Fiberglass with Bonded Steel Composite with Cathodic Protection Composite with Secondary Containment Copper Black Steel PVC Stainless Steel Double Wall Cathode Protected Steel Flexible Single Walled Piping Flexible Double Walled Piping Copper with Secondary Containment. PIPING LEAK DETECTION: None Manual Monitoring, Secondary Containment Electronic, Secondary Containment Manual Groundwater Sampling Electronic, Groundwater Statistical Inventory Analysis Continuous Electronic Vapor Monitoring. |

Facility: _______________________ City: ________________________ Application Date: ______________

Copy these pages as needed for additional tanks.

Page 4 of 4, Set _____ of _____

SIDE AND END VIEWS PLAN

(These are the plans to be used to construct the facility!)

Show All of the Following on this Diagram: >Base Material >Emergency Vents >Piping >Protection >Buildings and Dimensions >Ground and Foundation >Primary Chamber >Routing of Piping >Fire Extinguishing >Building Construction Type >Type of Secondary >Type and Size >Piping Connections >From Flooding >Building Materials Containment >Interstitial Space >Valves >From Collision >Floor Plan >Dike >Type and Size >Anti-Siphon >From Tampering >Exit Routes and Exit Signs >Construction Material >Pressure Relief >Alarm System >Inside Dimensions >Electrical Equipment >Break-away >Tank Marking >Emergency Lights >Capacity >Emergency Disconnects >Piping Supports >”No Smoking” >Sprinkler System Specs >Drain and Valve >Spill Bucket >Product Name >Secondary Containment >Remote Impounding >Loading Docks >NFPA 704 Placard >Tank Fill and Vent >Tanks >Vehicle Containment >Color Code >Tank Supports >Bonding Connection >On Tanks >Roofs and Canopies >Normal Vents >Self Closing Valves >On Piping >Construction Plans >Type and Size >Height Above Top of Tank >Height Above Ground >Vent Termination

Facility: _______________________ City: ________________________ Application Date: ______________

SITE PLAN

(This is the plan to be used to construct the facility!)

| Show the Location of All of the Following on this Plan: >Tanks and Dikes >Electrical Controls >Loading & Unloading >Buildings >Emergency Disconnects Piping >Property Lines >Fire Extinguishing >Sump Leak Detection >Public Ways Equipment >Remote Impounding >Dispensers >Security Features >Designated Smoking Area >Propane Storage >Collision Protection | Show the Distance from the Tanks to the following on this plan: >Buildings >Other Tanks >Property Lines >Dispensers >Public Ways >Propane Storage | Indicate NORTH With Arrow |
| --- | --- | --- |

Facility: _______________________ City: ________________________ Application Date: ______________

Section A-1 If you answer “Yes” to any of the following questions, your facility is exempt from the siting restrictions. Yes No 1. Was the tank facility installed before September 30, 2008? 2. Will the facility be used solely to store heating oil that is consumed on site, not resold? 3. Is the facility replacing an aboveground oil storage facility that was installed before September 30, 2008 that is on the same property? 4. Is the facility replacing or expanding an underground oil storage facility that was registered on or before September 30, 2008 and is presently on the same property? If “Yes” enter the DEP Registration Number:______________

Section A-2 If you answered “No” to all the questions in A-1, complete this section. 1. Will any portion of the facility be installed after September 30, 2008? (If “No”, Section A-2 does not apply to the tank(s) you are installing.) 2. Will any portion of the facility be located within 300 feet of a private well or water supply? (This does not include a private well located on the same lot as the facility and serving only users living on that property.) 3. Will any portion of the facility be located within the source water protection area of a public drinking water well mapped by the Department of Human Services or within 1000 feet of a public water well, whichever is greater? Maps of source water protection areas are available on the internet at www.maine.gov/dhs/eng/water/index.htm. Public water supplies are defined as any well or water supply where water is obtained, sold, furnished, or distributed to the public for human consumption. The well or water supply must meet one or more of the following requirements to be a public water supply: • Serves more than 15 connections, OR • Regularly Serves at least 25 individuals daily for at least 60 days of the year, OR • Provides bottled water for sale where the water is pumped from on site.

4. Does the well or water supply serve a school or community water supply system? (A school is an institution for the formal classroom instruction of children in grades k-12. A community water system is a public water system that serves at least 15 service connections used by year-round residents or regularly serves at least 25 year-round residents.) 5. Will any portion of the facility be located within a mapped significant sand and gravel aquifer? As of July 1, 2010, Maine law prohibits installation of ASTs within significant sand and gravel aquifers mapped by the Maine Geological Survey unless a variance is obtained from the Department of Environmental Protection (DEP). If the answer to #2 or #4 above is “Yes”, a new aboveground oil storage facility may not be installed unless the applicant proves there is no hydrogeologic connection between the proposed facility and the water supply at issue. Contact DEP at (207) 287-7688 to obtain information on the procedures to follow to determine if a hydrogeologic connection exists. If the answer to #3 is “Yes” and the answer to #4 is “No”, then a variance from the siting restriction may be granted upon written application to DEP if DEP determines that the proposed installation is designed to exceed minimum regulatory requirements and will effectively minimize releases of oil and the likelihood of drinking water contamination. If the answer to #5 is “YES”, Please review Chapter 692, Section (4)-(B) through (E) to determine if a variance may be applicable for the proposed site. Contact DEP for an application for a variance. For questions about the siting law, please call (207) 287-7688 or visit the DEP Drinking Water Protection website: www.maine.gov/dep/rwm/drinkingwater/index.htm