Forms and Agreements 1:  Definitions

The following words and terms when used in the Level 1, Level 2, Level 3 or Level 4 interconnection applications, agreements, or attachments thereto shall have the following meanings, unless the context clearly indicates otherwise.

- Annualized Period. "Annualized Period" means a period of 12 consecutive monthly billing periods. A Customer- Generator's first Annualized Period begins on the first day of the first full monthly billing period after which the Customer-Generator's facility is interconnected and is generating electricity.

- Applicant. "Applicant" means a person who has filed an application to interconnect a Customer-Generator Facility to an Electric Delivery System.

- Business Day. “Business Day” means any day except a Saturday, Sunday, a Federal Reserve Bank Holiday, or a holiday recognized by the State of Maine, A Business Day shall open at 8:00 a.m. and Close at 5:00 p.m. Eastern Prevailing Time.

- Certificate of Completion. “Certificate of Completion” means the standard form included with these forms and agreements as Forms and Agreements 6 that indicate the facility has been inspected and found in compliance with local codes.

- Company. "Company" means an electric Company operating a distribution system. Also called "T & D Utility.”

- Competitive Electricity Provider. “Competitive Electricity Provider” or “CEP” means a marketer, broker, aggregator, and any entity selling electricity to the public at retail who is licensed pursuant to Chapter 305 of the PUC’s rules. This term does not include T & D Utility’s, as defined herein.

- Customer. "Customer" means any entity interconnected to the utility Company system for the purpose of receiving [or exporting] electric power from [or to] the T & D Utility system.

- Customer-Generator. "Customer-Generator" means a residential or commercial Customer that generates electricity, typically on the Customer's side of the meter.

- Customer-Generator Facility. "Customer-Generator Facility" means the equipment used by a Customer-Generator to generate, manage and monitor electricity. A Customer-Generator Facility typically includes an electric generator and/or an Equipment Package, as defined herein.

- Electric Delivery System. "Electric Delivery System" or "EDS" means the infrastructure constructed and maintained by a T & D Utility, as defined herein, to deliver electric service to end-users.

- Equipment Package. "Equipment Package" means a group of components connecting an electric generator with an Electric Delivery System, and includes all interface equipment including switchgear, inverters or other interface devices. An Equipment Package may include an integrated generator or electric source.

- FERC. "FERC" means the U.S. Federal Energy Regulatory Commission.

- Force Majeure Event. "Force Majeure Event" means, for the purposes of this agreement, any event: (a) that is beyond the reasonable control of the affected party; and (b) that the affected party is unable to prevent or provide against by exercising reasonable diligence, including the following events or circumstances, but only to the extent they satisfy the preceding requirements: acts of war, public disorder, insurrection, or rebellion; floods, hurricanes, earthquakes, lightning, storms, and other natural calamities; explosions or fires; strikes, work stoppages, or labor disputes; embargoes; and sabotage.

- IEEE. "IEEE" means the "Institute of Electrical and Electronic Engineers."

- IEEE Standards. "IEEE standards" means the standards published by the Institute of Electrical and Electronic Engineers, available at www.ieee.org.

- Interconnection Agreement. "Interconnection Agreement" means an agreement between a Customer-Generator and a T & D Utility, which governs the connection of the Customer-Generator Facility to the Electric Delivery System, as well as the ongoing operation of the Customer-Generator Facility after it is connected to the system. An Interconnection Agreement shall follow the standard form agreement developed by the PUC and posted on the PUC's website.

- Interconnection Forms and Agreements. “Interconnection Forms and Agreements” or “Forms and Agreements” means the standard forms and agreements developed and adopted by the PUC by order and maintained on its website at http://www.maine.gov/mpuc/.

- Minor System Modifications. "Minor System Modifications" include activities such as changing the fuse in a fuse holder cut-out, changing the settings on a circuit recloser and other activities that usually entail less than 4 hours of work and $1000 in materials.

- Point of Common Coupling. "Point of Common Coupling" means the point in the interconnection of a Customer-Generator Facility with an Electric Delivery System at which the harmonic limits are applied and shall have the same meaning as in IEEE Standard 1547.

- PUC. "PUC" means the state regulatory authority over electricity utilities or any successor agency.

- Queue Position. "Queue Position" Queue Position of each Interconnection Request will be used to determine the order of interconnection review in those circumstances where one pending interconnection application could affect the analysis of other pending interconnection applications as well as any cost responsibility for the facilities necessary to accommodate the generator interconnection. Queue Position is based on the date of receipt of a completed application.

- Spot Network. "Spot Network" means a type of Electric Delivery System that uses two or more inter-tied transformers to supply an electrical network circuit. A Spot Network is generally used to supply power to a single Customer or to a small group of Customers, and has the same meaning as the term is used in IEEE standard 1547.

- Transmission and Distribution Utility. ‘Transmission and Distribution Utility” or “T & D Utility” means an electric utility that distributes electricity to end users within the State of Maine

Forms and Agreements 2:  Level 1 Application for Certified, Inverter-Based

Generating Facilities Not Greater than 10 kW

This Application is considered complete when it provides all applicable and correct information required below. Additional information to evaluate the Application may be required.

Processing Fee: A fee of $20 must accompany this Application.

Interconnection Customer

Name: ________________________________________________________________

Contact Person:

Address:

City, State, Zip:

Telephone (Day):

Telephone (Evening):

Fax:

E-Mail Address:

Contact (if different from Interconnection Customer)

Name:

Address:

City, State, Zip:

Telephone (Day):

Telephone (Evening):

Fax:

E-Mail Address:

Owner of the facility (include percent ownership by any electric utility):

Small Generating Facility Information

Location (if different from above):

Electric Service Company:

Account Number:

Small Generator 10 kW Inverter Process

Inverter Manufacturer: _____________________ 	Model: 7________________________

Nameplate Rating: ___________(kW) (kVA) (AC Volts)

Single Phase _______ Three Phase _____

System Design Capacity: _________ (kW) _______ (kVA)

Prime Mover: Photovoltaic / Reciprocating Engine / Fuel Cell / Turbine / Other

Energy Source: Solar / Wind / Hydro / Diesel / Natural Gas / Fuel Oil Other (describe) ____________

Is the equipment UL1741 Listed? Yes / No

If Yes, attach manufacturer's cut-sheet showing UL1741 listing

Estimated Installation Date: _____________ Estimated In-Service Date: ____________

The Level 1 Process is available only for inverter-based Generating Facilities no larger than 10 kW that meet the codes, standards, and certification requirements.

List components of the Small Generating Facility Equipment Package that are currently certified:

Equipment Type Certifying Entity

1.

2.

3.

4.

5.

Interconnection Customer Signature ___________________________________________

I hereby certify that, to the best of my knowledge, the information provided in this Application is true. I agree to abide by the Terms and Conditions for Level 1 interconnection for a Generating Facility No Larger than 10kW and return the Certificate of Completion (or other evidence of local code official approval), when the Small Generating Facility has been installed.

Signed: ________________________________________________________________

Title: 				Date:

Contingent Approval to Interconnect the Small Generating Facility

(For Company use only)

Interconnection of the Small Generating Facility is approved contingent upon the Terms and Conditions for Level 1 Generating Facility No Larger than 10 kW and return the Certificate of Completion (or other evidence of local code official approval), when the Small Generating Facility has been installed.

Company Signature: __________________________________________________

Title: 				Date:

Application ID number: __________________

Company waives inspection/witness test? Yes___No___

Forms and Agreements 3:  Level 1

Interconnection Agreement

This Agreement is made and entered into this ___ day of ______ by and between __________________, a _____________ organized and existing under the laws of the State of _____________, (''Interconnection Customer,'') and ___________________, a ____________________________, existing under the laws of the State of _________________________, ('' T & D Utility ''). Interconnection Customer and T & D Utility each may be referred to as a ''Party,'' or collectively as the ''Parties.''

Recitals:

Whereas, Interconnection Customer is proposing to develop a Small Generator Facility, or generating capacity addition to an existing Small Generator Facility, consistent with the Interconnection Request completed by Interconnection Customer on ________________; and

Whereas, Interconnection Customer desires to interconnect the Small Generator Facility with T & D Utility 's Electric Distribution System.

Now, therefore, in consideration of and subject to the mutual covenants contained herein, the Parties agree as follows:

1.0  Scope and Limitations of Agreement

1.1 	This Agreement shall be used for all approved Level 2, Level 3 and Level 4 Interconnection Requests according to the procedures set forth in the Standard Small Generator Interconnection Rule.

1.2	This Agreement governs the terms and conditions under which the Small Generator Facility will interconnect to, and operate in Parallel with, T & D Utility 's Electric Distribution System.

1.3	This Agreement does not constitute an agreement to purchase or deliver the Interconnection Customer's power.

  - Nothing in this Agreement is intended to affect any other agreement between T & D Utility and the Interconnection Customer. However, in the event that the provisions of this agreement are in conflict with the provisions of the T & D Utility tariff, the T & D Utility tariff shall control.

2.0	Construction of the Facility

The Customer may proceed to construct (including operational testing not to exceed two hours) the Generating Facility when the T & D Utility approves the Application and executes this Interconnection Agreement.

3.0	Interconnection and Operation

The Customer may operate Generating Facility and interconnect with the Company's electric system once all of the following have occurred:

3.1 	Upon completing construction, the Customer will cause the Generating Facility to be inspected or otherwise approved by the appropriate local electrical wiring inspector with jurisdiction, and

3.2	The Customer returns the Certificate of Completion (or other evidence of local code official approval) to the Company, and

3.3 	The Company has either:

3.3.1	Witnessed the satisfactory Commissioning. All witnessing and inspections must be conducted by the Company, at its own expense, and returned the Certificate of Completion (or other evidence of local code official approval), or

3.3.2	 If the Company does not schedule an inspection of the Small Generating Facility, the witness test is deemed waived (unless the Parties agree otherwise); or

3.3.3 	The Company waives the right to inspect the Small Generating Facility.

3.4 	The Company has the right to disconnect the Small Generating Facility in the event of improper installation.

4.0 	Safe Operations and Maintenance

The Customer shall be fully responsible to operate, maintain, and repair the Generating Facility as required to ensure that it complies at all times with the interconnection standards to which it has been certified.

5.0	Access

The Company shall have access to the metering equipment of the Generating Facility at all times. The Company shall provide reasonable notice to the Customer when possible prior to using its right of access.

6.0	Disconnection

The Company may temporarily disconnect the Generating Facility upon the following conditions:

5.1	For scheduled outages upon reasonable notice.

5.2	For unscheduled outages or emergency conditions.

5.3 	If the Generating Facility does not operate in the manner consistent with these Terms and Conditions.

5.4	 The Company shall inform the Customer in advance of any scheduled disconnection, or as is reasonable after an unscheduled disconnection.

7.0	 Indemnification

The Parties shall at all times indemnify, defend, and hold the other Party harmless from, any and all damages, losses, claims, including claims and actions relating to injury to or death of any person or damage to property, demand, suits, recoveries, costs and expenses, court costs, attorney fees, and all other obligations by or to third Parties, arising out of or resulting from the indemnified Party’s action or inactions of its obligations under this agreement on behalf of the indemnifying Party, except in cases of gross negligence or intentional wrongdoing by the indemnified Party.

8. 0 	Insurance

The Customer is not required to provide general liability insurance coverage as part of this Agreement, or any other Company requirement.

9.0 	Limitation of Liability

Each party's liability to the other party for any loss, cost, claim, injury, liability, or expense, including reasonable attorney's fees, relating to or arising from any act or omission in its performance of this Agreement, shall be limited to the amount of direct damage actually incurred. In no event shall either party be liable to the other party for any indirect, incidental, special, consequential, or punitive damages of any kind whatsoever, except as allowed under paragraph 6.0.

10.0	Effective Date, Term, and Termination

10.1 Effective Date

This Agreement shall become effective upon execution by the Parties.

10.2 Term of Agreement

This Agreement shall become effective on the Effective Date and shall remain in effect perpetually, unless terminated earlier in accordance with the provisions of Section 10.1 of this Agreement.

  - Termination

The agreement to operate in parallel may be terminated under the following conditions:

10.1.1	By the Customer

By providing written notice to the Company.

10.1.2 By the Company

If the Generating Facility fails to operate for any consecutive 12 month period or the Customer fails to remedy a violation of these Terms and Conditions.

10.1.3 Permanent Disconnection

In the event this Agreement is terminated, the Company shall have the right to disconnect its facilities or direct the Customer to disconnect its Small Generating Facility.

10.4 Survival Rights

This Agreement shall continue in effect after termination to the extent necessary to allow or require either Party to fulfill rights or obligations that arose under the Agreement.

11.0 	Notices

Any written notice, demand, or request required or authorized in connection with this Agreement ("Notice") shall be deemed properly given if delivered in person or sent by first class mail, postage prepaid, to the person specified below:

Company Name: ____________________

Address: _________________

City: ____________________

Phone: ___________________

FAX: ____________________

Customer Name: ____________________

Address: __________________

City: _____________________

Phone: ____________________

FAX: _____________________

12.0	Assignment/Transfer of Ownership of the Facility

This Agreement shall survive the transfer of ownership of the Generating Facility to a new owner when the new owner agrees in writing to comply with the terms of this Agreement and so notifies the Company.

13.0 Signatures

IN WITNESS WHEREOF, the Parties have caused this Agreement to be executed by their respective duly authorized representatives.

For [Utility Name]

Name: _____________________________________________________ Date: ______________	___________________________________________

Title: ______________________________________________________

For the Interconnection Customer

Name: _____________________________________________________ Date: ______________

Title: ______________________________________________________

Forms and Agreements 4:  Level 2, Level 3 and Level 4

Interconnection Application

A Customer-Generator applicant ("Applicant") hereby makes application to _____________ (Utility or T & D Utility) to install and operate a generating facility interconnected with the ______________ utility system. This application will be considered as an application for interconnection of generators under Expedited interconnection review provided the generator is not greater than 2 MW but shall serve as an Application for Standard interconnection review if greater than 2 MW or if Expedited review does not qualify the generator for interconnection.

Written applications should be submitted by mail, e-mail or fax to [[insert utility name]], as follows:

[Utility]:_________________________________________

[Utility's address]: _________________________________________

Fax Number: _________________________________________

E-Mail Address: _____________________________________________

[Utility] Contact Name: _______________________________________________

[Utility] Contact Title: _______________________________________________

An application is a Complete Application when it provides all applicable information required below. (Additional information to evaluate a request for interconnection may be required and will be so requested from the Interconnection Applicant by Utility after the application is deemed complete).

Section 1.  Applicant Information

Legal Name of Interconnecting Applicant (or, if an Individual, Individual's Name)

Name: __________________________________________________________

Mailing Address: _________________________________________________

City:  _____________________   State: __________________    Zip Code: ________________

Facility Location (if different from above):  _________________________________________

Telephone (Daytime): ________________

Telephone (Evening): ________________

Fax Number: ____________________________

E-Mail Address: ______________________________

______________________ 		_________________________________

(Utility) 		(Existing Account Number, if generator to be interconnected on the Customer side of a utility revenue meter)

Type of Interconnect Service Applied for (choose one):  ________ Network Resource, _______

Energy Only, ______ Load Response (no export) ________ Net metering

Section 2. Generator Qualifications

Data apply only to the Small Generating Facility, not the Interconnection Facilities.

Energy Source: ___ Solar ___ Wind ___ Hydro ___ Hydro Type (e.g. Run-of-River):_____________

Diesel ___ Natural Gas ___ Fuel Oil ___ Other (state type) ___________________________

Prime Mover: Fuel Cell   Recip. Engine    Gas Turb.   Steam Turb.   Microturbine   PV    Other

Type of Generator: ____Synchronous ____Induction ____ Inverter ____

Generator Nameplate Rating: ________kW (Typical) Generator Nameplate kVA: _______

Interconnection Customer or Customer-Site Load: _________________kW (if none, so state)

Typical Reactive Load (if known): _________________

Maximum Physical Export Capability Requested: ______________ kW

List components of the Small Generating Facility Equipment Package that are currently certified:

Equipment Type               Certifying Entity

1.

2.

3.

4.

5.

Is the prime mover compatible with the certified protective relay package? ____Yes ____No

Generator (or solar collector)

Manufacturer, Model Name & Number:

Version Number:

Nameplate Output Power Rating in kW: (Summer) _____________ (Winter) ______________

Nameplate Output Power Rating in kVA: (Summer) _____________ (Winter) ______________

Individual Generator Power Factor

Rated Power Factor: Leading: _____________Lagging: _______________

Total Number of Generators in wind farm to be interconnected pursuant to this

Interconnection Request: __________ Elevation: ______ ___Single phase ___Three phase ___

Inverter Manufacturer, Model Name & Number (if used): _____________________________________

List of adjustable set points for the protective equipment or software: __________________________

Note: A completed Power Systems Load Flow data sheet must be supplied with the Interconnection Request.

Small Generating Facility Characteristic Data (for inverter-based machines)

Max design fault contribution current: 			Instantaneous or RMS?

Harmonics Characteristics:

Start-up requirements:

Small Generating Facility Characteristic Data (for rotating machines)

RPM Frequency: _____________

(*) Neutral Grounding Resistor (If Applicable): ____________

Synchronous Generators:

Direct Axis Synchronous Reactance, Xd: _______ P.U.

Direct Axis Transient Reactance, X' d: ___________P.U.

Direct Axis Subtransient Reactance, X" d: ______________P.U.

Negative Sequence Reactance, X2: _________ P.U.

Zero Sequence Reactance, X0: ____________ P.U.

KVA Base: __________________________

Field Volts: ______________

Field Amperes: ______________

Induction Generators:

Motoring Power (kW): ______________

I 2t or K (Heating Time Constant): ______________

Rotor Resistance, Rr: ______________

Stator Resistance, Rs: ______________

Stator Reactance, Xs: ______________

Rotor Reactance, Xr: ______________

Magnetizing Reactance, Xm: ______________

Short Circuit Reactance, Xd": ______________

Exciting Current: ______________

Temperature Rise: ______________

Frame Size: ______________

Design Letter: ______________

Reactive Power Required In Vars (No Load): ______________

Reactive Power Required In Vars (Full Load): ______________

Total Rotating Inertia, H: _____________ Per Unit on kVA Base

Note: Please contact the T & D Utility prior to submitting the Interconnection Request to determine if the specified information above is required.

Excitation and Governor System Data for Synchronous Generators Only

Provide appropriate IEEE model block diagram of excitation system, governor system and power system stabilizer (PSS) in accordance with the regional reliability council criteria. A PSS may be determined to be required by applicable studies. A copy of the manufacturer's block diagram may not be substituted.

Section 3. Interconnection Facilities Information

Will a transformer be used between the generator and the Point of Common Coupling? ___Yes ___No

Will the transformer be provided by the Interconnection Customer? ____Yes ____No

Transformer Data (If Applicable, for Interconnection Customer-Owned Transformer):

Is the transformer: ____single phase _____three phase? Size: ___________kVA

Transformer Impedance: _______percent on __________kVA Base

If Three Phase:

Transformer Primary: _____ Volts _____ Delta _____Wye _____ Wye Grounded

Transformer Secondary: _____ Volts _____ Delta _____Wye _____ Wye Grounded

Transformer Tertiary: _____ Volts _____ Delta _____Wye _____ Wye Grounded

Transformer Fuse Data (If Applicable, for Interconnection Customer-Owned Fuse):

(Attach copy of fuse manufacturer's Minimum Melt and Total Clearing Time-Current Curves)

Manufacturer: __________________ Type: _______________ Size: ________Speed: ______________

Interconnecting Circuit Breaker (if applicable):

Manufacturer: ____________________________ Type: __________

Load Rating (Amps): _______ Interrupting Rating (Amps): ________ Trip Speed (Cycles): __________

Interconnection Protective Relays (If Applicable):

If Microprocessor-Controlled:

List of Functions and Adjustable Setpoints for the protective equipment or software:

Setpoint Function                           Minimum                         Maximum

1. ____________________	_____________________	____________________

2. ____________________	_____________________	_____________________

3. ____________________	_____________________	_____________________

4. ____________________	_____________________	_____________________

5. ____________________	_____________________	_____________________

6. ____________________	_____________________	_____________________

If Discrete Components:

(Enclose Copy of any Proposed Time-Overcurrent Coordination Curves)

Manufacturer: 		Type: 			Style/Catalog No.: 			Proposed Setting:

Manufacturer: 		Type:			Style/Catalog No.:			Proposed Setting:

Manufacturer: 		Type: 			Style/Catalog No.: 			Proposed Setting:

Manufacturer: 		Type: 			Style/Catalog No.:			Proposed Setting:

Manufacturer: 		Type: 			Style/Catalog No.:			Proposed Setting:

Current Transformer Data (If Applicable):

(Enclose Copy of Manufacturer's Excitation and Ratio Correction Curves)

Manufacturer:

Type: Accuracy Class: Proposed Ratio Connection: ____

Manufacturer:

Type: Accuracy Class: Proposed Ratio Connection: ____

Potential Transformer Data (If Applicable):

Manufacturer:

Type: Accuracy Class: Proposed Ratio Connection: ____

Manufacturer:

Type: Accuracy Class: Proposed Ratio Connection: ____

Section 4. General Information

Enclose copy of site electrical one-line diagram showing the configuration of all Small Generating Facility equipment, current and potential circuits, and protection and control schemes. This one-line diagram must be signed and stamped by a licensed Professional Engineer if the Small Generating Facility is larger than 50 kW. Is One-Line Diagram

Enclosed? ____Yes ____No

Enclose copy of any site documentation that indicates the precise physical location of the proposed Small Generating Facility (e.g., USGS topographic map or other diagram or documentation).

Proposed location of protective interface equipment on property (include address if different from the

Interconnection Customer's address) ___________________________________________________

Enclose copy of any site documentation that describes and details the operation of the protection and control schemes. Is Available Documentation Enclosed? ___Yes ____No

Enclose copies of schematic drawings for all protection and control circuits, relay current circuits, relay potential circuits, and alarm/monitoring circuits (if applicable).

Are Schematic Drawings Enclosed? ___Yes ____No

Section 5. Applicant Signature

I hereby certify that, to the best of my knowledge, all the information provided in the Interconnection

Application is true and correct.  I also agree to install a Warning Label provided by (utility) on or near my service meter location. Generating systems must be compliant with IEEE, NEC, ANSI, and UL standards, where applicable.  By signing below, the Applicant also certifies that the installed generating equipment meets the appropriate preceding requirement(s) and can supply documentation that confirms compliance.

Signed: ___________________________________________________________________ Date:________________

Section 6. Information Required Prior to Physical Interconnection

(Not required as part of the application, unless available at time of application.)

Installing Electrician:  ______________________   Firm:  ______________________

License No.:  ___________

Mailing Address:  _______________________________________________________

City:  ___________ State: ___________    Zip Code:  ___________ Telephone:  ___________

Installation Date:     ___________

Interconnection Date:  ___________

Signed (Inspector - if required):  ________________________________

Date: _________________________

(In lieu of signature of Inspector, a copy of the final inspection certificate may be attached)

Forms and Agreements 5:  Level 2, Level 3 and Level 4

Interconnection Agreement

This Agreement is made and entered into this ___ day of ______ by and between __________________, a _____________ organized and existing under the laws of the State of _________________, (''Interconnection Customer,'') and ___________________, a ____________________________, existing under the laws of the State of Maine, ('' T & D Utility ''). Interconnection Customer and T & D Utility each may be referred to as a ''Party,'' or collectively as the ''Parties.''

Recitals:

Whereas, Interconnection Customer is proposing to develop a Small Generator Facility, or generating capacity addition to an existing Small Generator Facility, consistent with the Interconnection Request completed by Interconnection Customer on ________________; and

Whereas, Interconnection Customer desires to interconnect the Small Generator Facility with T & D Utility 's Electric Distribution System.

Now, therefore, in consideration of and subject to the mutual covenants contained herein, the Parties agree as follows:

Article 1.  Scope and Limitations of Agreement

1.1 	This Agreement shall be used for all approved Level 2, Level 3, and Level 4 Interconnection Requests according to the procedures set forth in the Standard Small Generator Interconnection Rule.

1.2	This Agreement governs the terms and conditions under which the Small Generator Facility will interconnect to, and operate in Parallel with, T & D Utility 's Electric Distribution System.

  - This Agreement does not constitute an agreement to purchase or deliver the Interconnection Customer's power.

  - Nothing in this Agreement is intended to affect any other agreement between T & D Utility and the Interconnection Customer. However, in the event that the provisions of this agreement are in conflict with the provisions of the T & D Utility tariff, the T & D Utility tariff shall control.

  - Responsibilities of the Parties

    - The Parties shall perform all obligations of this Agreement in accordance with all Applicable Laws and Regulations, and Operating Requirements.

    - The Interconnection Customer shall construct, interconnect, operate and maintain its Small Generator Facility, and construct, operate, and maintain its Interconnection Equipment in accordance with the applicable manufacturer's recommended maintenance schedule, in accordance with this Agreement.

    - T & D Utility shall construct, own, operate, and maintain its Electric Distribution System and Interconnection Facilities in accordance with this Agreement.

    - The Interconnection Customer agrees to construct its facilities or systems in accordance with applicable specifications that meet or exceed the National Electrical Code, the American National Standards Institute, IEEE, Underwriters Laboratories, and any other Operating Requirements.

    - Each Party shall operate, maintain, repair, and inspect, and shall be fully responsible for the facilities that it now or subsequently may own unless otherwise specified in the Exhibits to this Agreement and shall do so in a manner as to reasonably minimize the likelihood of a disturbance adversely affecting or impairing the other party

    - Each Party shall be responsible for the safe installation, maintenance, repair and condition of their respective lines and appurtenances on their respective sides of the Point of Common Coupling.

  - Parallel Operation Obligations Once the Small Generator Facility has been authorized to commence parallel operation, the Interconnection Customer shall abide by all written rules and procedures developed by the T & D Utility which pertain to the parallel operation of the Small Generator Facility, copies of which are provided as an Exhibit [ ] to this Agreement.

  - Reactive Power

The Interconnection Customer shall design its Small Generator Facility to maintain a composite power delivery at continuous rated power output at the Point of Common Coupling at a power factor within the range of 0.95 leading to 0.95 lagging.

Article 2.  Inspection, Testing, Authorization, and Right of Access

2.1	Equipment Testing and Inspection

The Interconnection Customer shall test and inspect its Small Generator Facility and Interconnection Facilities prior to interconnection, and in accordance with IEEE 1547 Standards.

2.2   Certificate of Completion

Prior to commencing parallel operation, the Interconnection Customer shall provide T & D Utility with a Certificate of Completion in the form of Attachment 6 of the Interconnection Forms and Agreements. The Certificate of Completion must either be signed by an electrical inspector with the authority to approve the interconnection or be accompanied by the electrical inspector’s own form authorizing interconnection of the Small Generation Facility.

2.3   Parallel Operation Obligations

The Interconnection Customer shall abide by all permissible written rules and procedures developed by the T & D

Utility which pertain to the parallel operation of the Small Generation Facility. In the event of conflicting     provisions the Interconnection Procedures shall take precedence over the T & D Utility’s rule or procedure. Copies of the Utilities rules and procedures for parallel operation are either provided as an Exhibit to this Agreement or an Exhibit that provides a reference to a website where copies of the rule or procedure is maintained.

2.2	Right of Access

At reasonable hours, and upon reasonable notice, or at any time without notice in the event of an emergency or hazardous condition, Company shall have access to Customer's premises for any reasonable purpose in connection with the performance of the obligations imposed on it by this Agreement or if necessary to meet its legal obligation to provide service to its Customers.

Article 3.  Effective Date, Term, Termination, and Disconnection

  - Effective Date

This Agreement shall become effective upon execution by the Parties.

3.2	Term of Agreement

This Agreement shall become effective on the Effective Date and shall remain in effect perpetually, unless terminated earlier in accordance with Article 3.3 of this Agreement.

3.3	Termination

No termination shall become effective until the Parties have complied with all Applicable Laws and Regulations applicable to such termination.

3.3.1 	The Interconnection Customer may terminate this Agreement at any time by giving T & D Utility 20 Business Days written notice.

3.32	Either Party may terminate this Agreement after Default pursuant to Article 6.6.

3.33	Upon termination of this Agreement, the Small Generator Facility will be disconnected from T & D Utility’s Electric Distribution System. The termination of this Agreement shall not relieve either Party of its liabilities and obligations, owed or continuing at the time of the termination.

    - The provisions of this Article shall survive termination or expiration of this Agreement.

  - Temporary Disconnection

The T & D Utility may temporarily disconnect the Small Generator Facility from its Electric Distribution System for so long as reasonably necessary in the event one or more of the following conditions or events occurs:

    - Emergency Conditions

"Emergency Condition" shall mean a condition or situation: (1) that in the judgment of the Party making the claim is imminently likely to endanger life or property; or (2) that, in the case of T & D Utility, is imminently likely (as determined in a non-discriminatory manner) to cause a material adverse effect on the security of, or damage to the Electric Distribution System, T & D Utility 's Interconnection Facilities or (3) that, in the case of the Interconnection Customer, is imminently likely (as determined in a non-discriminatory manner) to cause a material adverse effect on the security of, or damage to, the Small Generator Facility or the Interconnection Equipment . Under Emergency Conditions, T & D Utility or the Interconnection Customer may immediately suspend interconnection service and temporarily disconnect the Small Generator Facility. T & D Utility shall notify the Interconnection Customer promptly when it becomes aware of an Emergency Condition that may reasonably be expected to affect the Interconnection Customer's operation of the Small Generator Facility. The Interconnection Customer shall notify T & D Utility promptly when it becomes aware of an Emergency Condition that may reasonably be expected to affect T & D Utility’s Electric Distribution System. To the extent information is known, the notification shall describe the Emergency Condition, the extent of the damage or deficiency, the expected effect on the operation of both Parties' facilities and operations, its anticipated duration, and the necessary corrective action.

    - Routine Maintenance, Construction, and Repair

T & D Utility may interrupt interconnection service or curtail the output of the Small Generator Facility and temporarily disconnect the Small Generator Facility from T & D Utility’s Electric Distribution System when necessary for routine maintenance, construction, and repairs on T & D Utility’s Electric Distribution System. T & D Utility shall provide the Interconnection Customer with five Business Days notice prior to such interruption. T & D Utility shall use reasonable efforts to coordinate such reduction or temporary disconnection with the Interconnection Customer.

    - Forced Outages

During any forced outage, T & D Utility may suspend interconnection service to effect immediate repairs on T & D Utility’s Electric Distribution System. T & D Utility shall use reasonable efforts to provide the Interconnection Customer with prior notice. If prior notice is not given, T & D Utility shall, upon request, provide the Interconnection Customer written documentation after the fact explaining the circumstances of the disconnection.

    - Adverse Operating Effects

T & D Utility shall provide the Interconnection Customer with a written notice of its intention to disconnect the Small Generator Facility if, based on Good Utility Practice, the T & D Utility determines that operation of the Small Generator Facility will likely cause disruption or deterioration of service to other Customers served from the same electric system, or if operating the Small Generator Facility could cause damage to T & D Utility’s Electric Distribution System. Supporting documentation used to reach the decision to disconnect shall be provided to the Interconnection Customer upon request. T & D Utility may disconnect the Small Generator Facility if, after receipt of the notice, the Interconnection Customer fails to remedy the adverse operating effect within a reasonable time which shall be at least five Business Days from the date the Interconnection Customer receives the T & D Utility’s written notice supporting the decision to disconnect, unless Emergency Conditions exist in which case the provisions of Article 3.4.1 apply.

    - Modification of the Small Generator Facility

The Interconnection Customer must receive written authorization from T & D Utility before making any change to the Small Generator Facility that may have a material impact on the safety or reliability of the Electric Distribution System. Such authorization shall not be unreasonably withheld. Modifications shall be done in accordance with Good Utility Practice. If the Interconnection Customer makes such modification without T & D Utility’s prior written authorization, the latter shall have the right to temporarily disconnect the Small Generator Facility.

    - Reconnection

The Parties shall cooperate with each other to restore the Small Generator Facility, Interconnection Facilities, and T & D Utility 's Electric Distribution System to their normal operating state as soon as reasonably practicable following a temporary disconnection.

Article 4.  Cost Responsibility for Interconnection Facilities and Distribution Upgrades

  - Interconnection Facilities

    - The Interconnection Customer shall pay for the cost of the Interconnection Facilities itemized in the Exhibits to this Agreement. If a Facilities Study was performed, T & D Utility shall identify its Interconnection Facilities necessary to safely interconnect the Small Generator Facility with T & D Utility's Electric Distribution System, the cost of those facilities, and the time required to build and install those facilities.

    - The Interconnection Customer shall be responsible for its share of all reasonable expenses, including overheads, associated with (1) owning, operating, maintaining, repairing, and replacing its Interconnection Equipment, and (2) operating, maintaining, repairing, and replacing T & D Utility’s Interconnection Facilities as set forth in the Exhibits to this Agreement.

  - Distribution Upgrades

T & D Utility shall design, procure, construct, install, and own any Distribution Upgrades. The actual cost of the Distribution Upgrades, including overheads, shall be directly assigned to the Interconnection Customer.

Article 5.  Billing, Payment, Milestones, and Financial Security

  - Billing and Payment Procedures and Final Accounting

    - T & D Utility shall bill the Interconnection Customer for the design, engineering, construction, and procurement costs of T & D Utility provided Interconnection Facilities and Distribution Upgrades contemplated by this Agreement as set forth in the Exhibits to this Agreement, on a monthly basis, or as otherwise agreed by the Parties. The Interconnection Customer shall pay each bill within thirty (30) calendar days of receipt, or as otherwise agreed to by the Parties.

    - Within ninety (90) calendar days of completing the construction and installation of T & D Utility 's Interconnection Facilities and Distribution Upgrades described in the Exhibits to this Agreement, T & D Utility shall provide the Interconnection Customer with a final accounting report of any difference between (1) the actual cost incurred to complete the construction and installation and the budget estimate provided to the Interconnection Customer and a written explanation for any significant variation. (2) the Interconnection Customer's previous deposit and aggregate payments to T & D Utility for such Interconnection Facilities and Distribution Upgrades. If the Interconnection Customer's cost responsibility exceeds its previous deposit and aggregate payments, T & D Utility shall invoice the Interconnection Customer for the amount due and the Interconnection Customer shall make payment to T & D Utility within thirty (30) calendar days. If the Interconnection Customer's previous deposit and aggregate payments exceed its cost responsibility under this Agreement, T & D Utility shall refund to the Interconnection Customer an amount equal to the difference within thirty (30) calendar days of the final accounting report.

  - Interconnection Customer Deposit

At least twenty (20) Business Days prior to the commencement of the design, procurement, installation, or construction of a discrete portion of T & D Utility 's Interconnection Facilities and Distribution Upgrades, the Interconnection Customer shall provide T & D Utility with a deposit equal to 50 percent of the cost estimated for its Interconnection Facilities prior to its beginning design of such facilities.

Article 6. Assignment, Liability, Indemnity, Force Majeure, Consequential Damages, and Default

6.1	Assignment

This Agreement may be assigned by either Party upon fifteen (15) Business Days prior written notice, and with the opportunity to object by the other Party.  When required, consent to assignment shall not be unreasonably withheld; provided that:

    - Either Party may assign this Agreement without the consent of the other Party to any affiliate of the assigning Party with an equal or greater credit rating and with the legal authority and operational ability to satisfy the obligations of the assigning Party under this Agreement;

    - The Interconnection Customer shall have the right to assign this Agreement, without the consent of T & D Utility, for collateral security purposes to aid in providing financing for the Small Generator Facility;

    - Any attempted assignment that violates this Article is void and ineffective. Assignment shall not relieve a Party of its obligations, nor shall a Party's obligations be enlarged, in whole or in part, by reason thereof. An assignee is responsible for meeting the same obligations as the Interconnection Customer.

  - Limitation of Liability

Each Party's liability to the other Party for any loss, cost, claim, injury, liability, or expense, including reasonable attorney's fees, relating to or arising from any act or omission in its performance of this Agreement, shall be limited to the amount of direct damage actually incurred. In no event shall either Party be liable to the other Party for any indirect, special, consequential, or punitive damages, except as authorized by this Agreement.

  - Indemnity

    - This provision protects each Party from liability incurred to third Parties as a result of carrying out the provisions of this Agreement. Liability under this provision is exempt from the general limitations on liability found in Article 6.2.

    - The Parties shall at all times indemnify, defend, and hold the other Party harmless from, any and all damages, losses, claims, including claims and actions relating to injury to or death of any person or damage to property, demand, suits, recoveries, costs and expenses, court costs, attorney fees, and all other obligations by or to third Parties, arising out of or resulting from the indemnified Party's action or failure to meet its obligations under this Agreement on behalf of the indemnifying Party, except in cases of gross negligence or intentional wrongdoing by the indemnified Party.

    - If an indemnified person is entitled to indemnification under this Article as a result of a claim by a third party, and the indemnifying Party fails, after notice and reasonable opportunity to proceed under this Article, to assume the defense of such claim, such indemnified person may at the expense of the indemnifying Party contest, settle or consent to the entry of any judgment with respect to, or pay in full, such claim.

    - If an indemnifying party is obligated to indemnify and hold any indemnified person harmless under this Article, the amount owing to the indemnified person shall be the amount of such indemnified person's actual loss, net of any insurance or other recovery.

    - Promptly after receipt by an indemnified person of any claim or notice of the commencement of any action or administrative or legal proceeding or investigation as to which the indemnity provided for in this Article may apply, the indemnified person shall notify the indemnifying party of such fact. Any failure of or delay in such notification shall not affect a Party's indemnification obligation unless such failure or delay is materially prejudicial to the indemnifying party.

  - Consequential Damages

Neither Party shall be liable under any provision of this Agreement for any losses, damages, costs or expenses for any special, indirect, incidental, consequential, or punitive damages, including but not limited to loss of profit or revenue, loss of the use of equipment, cost of capital, cost of temporary equipment or services, whether based in whole or in part in contract, in tort, including negligence, strict liability, or any other theory of liability; provided, however, that damages for which a Party may be liable to the other Party under another agreement will not be considered to be special, indirect, incidental, or consequential damages hereunder.

  - Force Majeure

    - As used in this Article, a Force Majeure Event shall mean "any act of God, labor disturbance, act of the public enemy, war, acts of terrorism, insurrection, riot, fire, storm or flood, explosion, breakage or accident to machinery or equipment, any order, regulation or restriction imposed by governmental, military or lawfully established civilian authorities, or any other cause beyond a Party's control. A Force Majeure Event does not include an act of negligence or intentional wrongdoing."

    - If a Force Majeure Event prevents a Party from fulfilling any obligations under this Agreement, the Party affected by the Force Majeure Event (Affected Party) shall promptly notify the other Party of the existence of the Force Majeure Event. The notification must specify in reasonable detail the circumstances of the Force Majeure Event, its expected duration, and the steps that the Affected Party is taking to mitigate the effects of the event on its performance, and if the initial notification was verbal, it should be promptly followed up with a written notification. The Affected Party shall keep the other Party informed on a continuing basis of developments relating to the Force Majeure Event until the event ends. The Affected Party will be entitled to suspend or modify its performance of obligations under this Agreement (other than the obligation to make payments) only to the extent that the effect of the Force Majeure Event cannot be reasonably mitigated. The Affected Party will use reasonable efforts to resume its performance as soon as possible.

  - Default

    - No Default shall exist where such failure to discharge an obligation (other than the payment of money) is the result of a Force Majeure Event as defined in this Agreement, or the result of an act or omission of the other Party. Upon a Default, the non-defaulting Party shall give written notice of such Default to the defaulting Party. Except as provided in Article 6.6.2, the defaulting Party shall have 60 calendar days from receipt of the Default notice within which to cure such Default; provided however, if such Default is not capable of cure within 60 calendar days, the defaulting Party shall commence such cure within 20 calendar days after notice and continuously and diligently complete such cure within six months from receipt of the Default notice; and, if cured within such time, the Default specified in such notice shall cease to exist.

    - If a Default is not cured as provided for in this Article, or if a Default is not capable of being cured within the period provided for herein, the non-defaulting Party shall have the right to terminate this Agreement by written notice at any time until cure occurs, and be relieved of any further obligation hereunder and, whether or not that Party terminates this Agreement, to recover from the defaulting Party all amounts due hereunder, plus all other damages and remedies to which it is entitled at law or in equity. The provisions of this Article will survive termination of this Agreement.

Article 7.  Insurance

The Interconnection Customer may be required by the T & D Utility to carry liability insurance for its interconnection subject to the restrictions and limitations found in Maine Public Utility Commission Rule Ch. 324 §12(F). To the extent T & D Utility requires liability insurance, its requirements for the Interconnecting Customer and any required documentation of coverage shall be included herewith under Exhibit (  ).

Article 8.  Dispute Resolution (see provisions in the Maine Public Utility Commission’s Standard Small Generator Interconnection Rules)

Article 9.  Miscellaneous

9.1	Governing Law, Regulatory Authority, and Rules

The validity, interpretation and enforcement of this Agreement and each of its provisions shall be governed by the laws of the State of Maine, without regard to its conflicts of law principles. This Agreement is subject to all Applicable Laws and Regulations. Each Party expressly reserves the right to seek changes in, appeal, or otherwise contest any laws, orders, or regulations of a Governmental Authority.

9.2	Amendment

The Parties may amend this Agreement by a written instrument duly executed by both Parties.

9.3	No Third-Party Beneficiaries

This Agreement is not intended to and does not create rights, remedies, or benefits of any character whatsoever in favor of any persons, corporations, associations, or entities other than the Parties, and the obligations herein assumed are solely for the use and benefit of the Parties, their successors in interest and where permitted, their assigns.

  - Waiver

    - The failure of a Party to this Agreement to insist, on any occasion, upon strict performance of any provision of this Agreement will not be considered a waiver of any obligation, right, or duty of, or imposed upon, such Party.

    - Any waiver at any time by either Party of its rights with respect to this Agreement shall not be deemed a continuing waiver or a waiver with respect to any other failure to comply with any other obligation, right, duty of this Agreement. Termination or default of this Agreement for any reason by Interconnection Customer shall not constitute a waiver of the Interconnection Customer's legal rights to obtain an interconnection from T & D Utility. Any waiver of this Agreement shall, if requested, be provided in writing.

  - Entire Agreement

This Agreement, including all Exhibits, constitutes the entire Agreement between the Parties with reference to the subject matter hereof, and supersedes all prior and contemporaneous understandings or agreements, oral or written, between the Parties with respect to the subject matter of this Agreement. There are no other agreements, representations, warranties, or covenants which constitute any part of the consideration for, or any condition to, either Party's compliance with its obligations under this Agreement.

9.6	Multiple Counterparts

This Agreement may be executed in two or more counterparts, each of which is deemed an original but all constitute one and the same instrument.

9.7	No Partnership

This Agreement shall not be interpreted or construed to create an association, joint venture, agency relationship, or partnership between the Parties or to impose any partnership obligation or partnership liability upon either Party. Neither Party shall have any right, power or authority to enter into any agreement or undertaking for, or act on behalf of, or to act as or be an agent or representative of, or to otherwise bind, the other Party.

  - Severability

If any provision or portion of this Agreement shall for any reason be held or adjudged to be invalid or illegal or unenforceable by any court of competent jurisdiction or other Governmental Authority, (1) such portion or provision shall be deemed separate and independent, (2) the Parties shall negotiate in good faith to restore insofar as practicable the benefits to each Party that were affected by such ruling, and (3) the remainder of this Agreement shall remain in full force and effect.

  - Environmental Releases

Each Party shall notify the other Party, first orally and then in writing, of the release any hazardous substances, any asbestos or lead abatement activities, or any type of remediation activities related to the Small Generator Facility or the Interconnection Facilities, each of which may reasonably be expected to affect the other Party. The notifying Party shall (1) provide the notice as soon as practicable, provided such Party makes a good faith effort to provide the notice no later than 24 hours after such Party becomes aware of the occurrence, and (2) promptly furnish to the other Party copies of any publicly available reports filed with any governmental authorities addressing such events.

  - Subcontractors

Nothing in this Agreement shall prevent a Party from utilizing the services of any subcontractor as it deems appropriate to perform its obligations under this Agreement; provided, however, that each Party shall require its subcontractors to comply with all applicable terms and conditions of this Agreement in providing such services and each Party shall remain primarily liable to the other Party for the performance of such subcontractor.

9.10.1	The creation of any subcontract relationship shall not relieve the hiring Party of any of its obligations under this Agreement. The hiring Party shall be fully responsible to the other Party for the acts or omissions of any subcontractor the hiring Party hires as if no subcontract had been made; provided, however, that in no event shall T & D Utility be liable for the actions or inactions of the Interconnection Customer or its subcontractors with respect to obligations of the Interconnection Customer under this Agreement. Any applicable obligation imposed by this Agreement upon the hiring Party shall be equally binding upon, and shall be construed as having application to, any subcontractor of such Party.

    - The obligations under this Article will not be limited in any way by any limitation of subcontractor's insurance.

Article 10.  Notices

10.1	General

Unless otherwise provided in this Agreement, any written notice, demand, or request required or authorized in connection with this Agreement ("Notice") shall be deemed properly given if delivered in person, delivered by recognized national currier service, or sent by first class mail, postage prepaid, to the person specified below:

If to Interconnection Customer:

Interconnection Customer: _________________________________________

Attention: _________________________________

Address: ______________________________________________________

City: _______________________________ State:____________ Zip:_______

Phone: ________________ Fax: ________________ E-mail_______________

If to T & D Utility:

T & D Utility ____________________________________________________

Attention: _________________________________

Address: _________________________________________________________

City: ____________________________ State:_____________ Zip:_______

Phone: ________________ Fax: _________________E-mail______________

  - Billing and Payment

Billings and payments shall be sent to the addresses set out below:

Interconnection Customer: ___________________________________________

Attention: _________________________________

Address: _________________________________________________________

City: _______________________________ State:_____________ Zip:_______

T & D Utility: ___________________________________________

Attention: _________________________________

Address: _________________________________________________________

City: ______________________________ State:______________ Zip:_______

10.3	Designated Operating Representative

The Parties may also designate operating representatives to conduct the communications which may be necessary or convenient for the administration of this Agreement. This person will also serve as the point of contact with respect to operations and maintenance of the Party's facilities.

Interconnection Customer's

Operating representative:____________________________________________

Attention: _________________________________

Address: _________________________________________________________

City: ______________________________ State:_____________ Zip:_______

Phone: ________________ Fax: _________________E-Mail_______________

T & D Utility 's Operating Representative: _____________________________

Attention: ________________________________

Address: _________________________________________________________

City: _______________________________ State:______________ Zip:______

Phone: ________________ Fax: ________________

Article 11.  Signatures

IN WITNESS WHEREOF, the Parties have caused this Agreement to be executed by their respective duly authorized representatives.

For the Transmission Provider

Name:	___________________________________________

Title:	___________________________________________

Date:	___________________

For the Interconnection Customer

Name:	___________________________________________

Title:	___________________________________________

Date:	___________________

Exhibits (if any):

Forms and Agreements 6:  Certificate of Completion

See note below

Installation Information 				Check if owner-installed □

Interconnection Customer: _________________________Contact Person:

Mailing Address:

Location of Small Generator Facility (if different from above):

______________________________________________________

City: 						State:			 Zip Code:

Telephone (Daytime):				(Evening):

Facsimile Number:					E-Mail Address:

Electrician:

Name:

Mailing Address:

City: 						State: 			Zip Code:

Telephone (Daytime):				(Evening):

Facsimile Number:					E-Mail Address:

License number: ____________________________________

Application ID number: ____________________________

Electrical Inspection:

The system has been installed and inspected in compliance with the local Building/Electrical Code of ___________________________________  (Appropriate governmental authority)

Signed (Local Electrical Wiring Inspector, or attach signed electrical inspection):

Name (printed):								Date: ___________

T & D Utility  waives Witness Test?  Yes □	No □

T & D Utility Signature:

Title:

Date:

Final Approval of Interconnection Agreement

The Certificate of Completion has been received and final approval to interconnect the Small Generation Small Generator Facility is granted under the Standard Small Generator Interconnection Rule.

T & D Utility Signature:						Title: 			Date:

Note: Local code officials may be unwilling to sign this form if it is not typically used in their approval process. In those cases, this certificate should be supplanted with evidence of local code official approval as is the current local practice.

Forms and Agreements 7:  Feasibility, Impact and Facilities Study Agreements

This agreement is made and entered into this _________day of __________by and between _____________________________, a_______________________ organized and existing under the laws of the State of_________________________, (''Interconnection Customer,'') and _________________________________, a __________________________existing under the laws of the State of _____________________________, ('' T & D Utility ''). Interconnection Customer and T & D Utility each may be referred to as a ''Party,'' or collectively as the ''Parties.''

Recitals:

Whereas, Interconnection Customer is proposing to develop a Small Generating Facility or generating capacity addition to an existing Small Generating Facility consistent with the Interconnection Request completed by Interconnection Customer on_________________________________; and

Whereas, Interconnection Customer desires to interconnect the Generating Facility with T & D Utility 's System; and

Whereas, Interconnection Customer has requested T & D Utility to perform an Interconnection Feasibility Study to assess the feasibility of interconnecting the proposed Generating Facility to T & D Utility 's Electric Distribution System;

Now, Therefore, in consideration of and subject to the mutual covenants contained herein the Parties agree as follows:

- When used in this agreement, with initial capitalization, the terms specified shall have the meanings indicated. Terms used in this agreement with initial capitalization but not defined in this agreement shall have the meanings specified in Attachment 1 of the Standard Small Generator Interconnection Forms.

- Interconnection Customer elects and T & D Utility shall cause to be performed an Interconnection Feasibility Study consistent with § 11 of the Standard Small Generator Interconnection Rule.

- The scope of the Interconnection Feasibility Study shall be subject to the assumptions set forth in Attachment A to this agreement.

- The Interconnection Feasibility Study shall be based on the technical information provided by Interconnection Customer in the Interconnection Request, as may be modified as the result of the Scoping Meeting. T & D Utility reserves the right to request additional technical information from Interconnection Customer as may reasonably become necessary consistent with Good Utility Practice during the course of the Interconnection Feasibility Study.  If Interconnection Customer modifies its Interconnection Request, the time to complete the Interconnection Feasibility Study may be extended by agreement of the Parties.

- In performing the study, T & D Utility shall rely, to the extent reasonably practicable, on existing studies of recent vintage. The Interconnection Customer will not be charged for such existing studies; however, Interconnection Customer shall be responsible for charges associated with any new study or modifications to existing studies that are reasonably necessary to perform the Interconnection Feasibility Study.

- The Interconnection Feasibility Study report shall provide the following information:

6.1. 	Preliminary identification of any circuit breaker short circuit capability limits exceeded as a result of the interconnection,

6.2.  	Preliminary identification of any thermal overload or voltage limit violations resulting from the interconnection, and

6.3.  	Preliminary description and non-bonding estimated cost of facilities required to interconnect the Generating Facility to T & D Utility 's Electric Distribution System and to address the identified short circuit and power flow issues.

- T & D Utility may require a study deposit of the lesser of 100 percent of estimated non-binding good faith study costs or $1,000.

- The Interconnection Feasibility Study shall be completed and the results shall be transmitted to Interconnection Customer within thirty Calendar Days after this agreement is signed by the Parties.

- Study fees shall be based on actual costs and will be invoiced to Interconnection Customer after the study is transmitted to Interconnection Customer. The invoice shall include an itemized listing of employee time and costs expended on the study.

10.  Interconnection Customer shall pay any actual study costs that exceed the deposit without interest within thirty Calendar Days on receipt of the invoice. T & D Utility shall refund any excess amount without interest within thirty Calendar Days of the invoice.

In witness whereof, the Parties have caused this agreement to be duly executed by their duly authorized officers or agents on the day and year first above written.

[[Insert name of T & D Utility]]

Signed_____________________________________

Name (Printed): ____________________________Title____________________________

[[Insert name of Interconnection Customer]]

Signed _____________________________

Name (Printed): _______________________Title____________________________

Attachment to Interconnection Feasibility Study Agreement:

Assumptions Used in Conducting the Interconnection Feasibility Study

The Interconnection Feasibility Study will be based upon the information set forth in the Interconnection Request and agreed upon in the Scoping Meeting held on__________________________:

1.   Designation of Point of Interconnection and configuration to be studied.

2.   Designation of alternative Points of Interconnection and configuration.

[[Note: 1 and 2 are to be completed by the Interconnection Customer. Other assumptions (listed below) are to be provided by Interconnection Customer and T & D Utility.]]

Forms and Agreements 8: Interconnection System Impact Study Agreement

This agreement is made and entered into this _________day of __________by and between _____________________________, a_______________________ organized and existing under the laws of the State of _________, (''Interconnection Customer,'') and _________________________________, a __________________________existing under the laws of the State of ____________, ('' T & D Utility ''). Interconnection Customer and T & D Utility each may be referred to as a ''Party,'' or collectively as the ''Parties.''

Recitals:

Whereas, Interconnection Customer is proposing to develop a Small Generating Facility or generating capacity addition to an existing Small Generating Facility consistent with the Interconnection Request completed by Interconnection Customer on _____________________ and;

Whereas, Interconnection Customer desires to interconnect the Generating Facility with T & D Utility 's Electric Distribution System;

Whereas, T & D Utility has completed an Interconnection Feasibility Study and provided the results of said study to Interconnection Customer (This recital to be omitted if the Parties have agreed to forego the Interconnection Feasibility Study.);

Whereas, Interconnection Customer has requested T & D Utility to perform an Interconnection System Impact Study to assess the impact of interconnecting the Generating Facility to T & D Utility 's Electric Distribution System;

Now, therefore, in consideration of and subject to the mutual covenants contained herein the Parties agree as follows:

- When used in this agreement, with initial capitalization, the terms specified shall have the meanings indicated. Terms used in this agreement with initial capitalization but not defined in this agreement shall have the meanings specified in Attachment 1 of the Standard Small Generator Interconnection Forms.

- Interconnection Customer elects and T & D Utility shall cause to be performed an Interconnection System Impact Study consistent with §11 of the Standard Small Generator Interconnection Rule.

- The scope of the Interconnection System Impact Study shall be subject to the assumptions set forth in Attachment A to this agreement.

- The Interconnection System Impact Study will be based upon the results of the Interconnection Feasibility Study and the technical information provided by Interconnection Customer in the Interconnection Request. T & D Utility reserves the right to request additional technical information from Interconnection Customer as may reasonably become necessary consistent with Good Utility Practice during the course of the Interconnection System Impact Study. If Interconnection Customer modifies its designated Point of Interconnection, Interconnection Request, or the technical information provided therein is modified, the time to complete the Interconnection System Impact Study may be extended.

- The Interconnection System Impact Study report shall provide the following information:

5.1. 	Identification of any circuit breaker short circuit capability limits exceeded as a result of the interconnection,

5.2	 Identification of any thermal overload or voltage limit violations resulting from the interconnection,

5.3	 Identification of any instability or inadequately damped response to system disturbances resulting from the interconnection and

  - Description and non-binding, good faith estimated cost of facilities required to interconnect the Generating Facility to T & D Utility 's Electric Distribution System and to address the identified short circuit, instability, and power flow issues.

- T & D Utility may require a study deposit of the lesser of 50 percent of estimated non-binding good faith study costs or $3,000.

- The distribution Interconnection System Impact Study, if required, shall be completed and the results transmitted to Interconnection Customer within thirty Calendar Days after this agreement is signed by the Parties. The distribution Interconnection System Impact Study, if required, shall be completed and the results transmitted to Interconnection Customer within forty-five Calendar Days after this agreement is signed by the Parties, or in accordance with T & D Utility 's queuing procedures.

- Study fees shall be based on actual costs and will be invoiced to Interconnection Customer after the study is transmitted to Interconnection Customer. The invoice shall include an itemized listing of employee time and costs expended on the study.

- Interconnection Customer shall pay any actual study costs that exceed the deposit without interest within 30 Calendar Days on receipt of the invoice. T & D Utility shall refund any excess amount without interest within thirty Calendar Days of the invoice.

In witness thereof, the Parties have caused this agreement to be duly executed by their duly authorized officers or agents on the day and year first above written.

[[Insert name of T & D Utility]]

Signed ___________________________

Name (Printed): ____________________________Title____________________________

[[Insert name of Interconnection Customer]]

Signed _____________________________

Name (Printed): _______________________Title____________________________

Attachment to Interconnection System Impact Study Agreement:

Assumptions Used in Conducting the Interconnection System Impact Study

The Interconnection System Impact Study shall be based upon the results of the Interconnection Feasibility Study, subject to any modifications in accordance with Section 6.5 of the Standard Small Generator Interconnection Rule, and the following assumptions:

1.   Designation of Point of Interconnection and configuration to be studied.

2.   Designation of alternative Points of Interconnection and configuration.

[[Note: 1 and 2 are to be completed by the Interconnection Customer. Other assumptions (listed below) are to be provided by Interconnection Customer and T & D Utility.]]

Forms and Agreements 9: Interconnection Facilities Study Agreement

This agreement is made and entered into this _________day of __________by and between ____________________________, a _______________________ organized and existing under the laws of the State of _________________________, (''Interconnection Customer,'') and _________________________________, a __________________________existing under the laws of the State of _____________________________, ('' T & D Utility ''). Interconnection Customer and T & D Utility each may be referred to as a ''Party,'' or collectively as the ''Parties.''

Recitals:

Whereas, Interconnection Customer is proposing to develop a Small Generating Facility or generating capacity addition to an existing Small Generating Facility consistent with the Interconnection Request completed by Interconnection Customer on ____________________________________; and

Whereas, Interconnection Customer desires to interconnect the Generating Facility with T & D Utility 's Electric Distribution System;

Whereas, T & D Utility has completed an Interconnection System Impact Study and provided the results of said study to Interconnection Customer; and

Whereas, Interconnection Customer has requested T & D Utility to perform an Interconnection Facilities Study to specify and estimate the cost of the equipment, engineering, procurement and construction work needed to implement the conclusions of the Interconnection System Impact Study in accordance with Good Utility Practice to physically and electrically connect the Generating Facility to T & D Utility 's Electric Distribution System.

Now, therefore, in consideration of and subject to the mutual covenants contained herein the Parties agree as follows:

- When used in this agreement, with initial capitalization, the terms specified shall have the meanings indicated. Terms used in this agreement with initial capitalization but not defined in this agreement shall have the meanings specified in Attachment 1 of the Standard Small Generator Interconnection Forms.

- Interconnection Customer elects and T & D Utility shall cause an Interconnection Facilities Study consistent with §11 of the Standard Small Generator Interconnection Rule.

- The scope of the Interconnection Facilities Study shall be subject to data provided in Attachment A to this agreement.

- An Interconnection Facilities Study report (1) shall provide a description, estimated cost of (consistent with Attachment A), schedule for required facilities to interconnect the Generating Facility to T & D Utility 's Electric Distribution System and (2) shall address the short circuit, instability, and power flow issues identified in the Interconnection System Impact Study.

- T & D Utility may require a study deposit of the lesser of 50 percent of estimated non-binding good faith study costs or $10,000.

- In cases where no Upgrades are required, the Interconnection Facilities Study shall be completed and the results shall be transmitted to Interconnection Customer within thirty Calendar Days after this agreement is signed by the Parties. In cases where Upgrades are required, the Interconnection Facilities Study shall be completed and the results shall be transmitted to Interconnection Customer within forty- five Calendar Days after this agreement is signed by the Parties.

- Study fees shall be based on actual costs and will be invoiced to Interconnection Customer after the study is transmitted to Interconnection Customer. The invoice shall include an itemized listing of employee time and costs expended on the study.

- Interconnection Customer shall pay any actual study costs that exceed the deposit without interest within 30 Calendar Days on receipt of the invoice. T & D Utility shall refund any excess amount without interest within thirty Calendar Days of the invoice.

In witness whereof, the Parties have caused this agreement to be duly executed by their duly authorized officers or agents on the day and year first above written.

[[Insert name of T & D Utility]]

Signed ___________________________

Name (Printed): ____________________________Title____________________________

[[Insert name of Interconnection Customer]]

Signed _____________________________

Name (Printed): _______________________Title____________________________

Attachment to Interconnection Facilities Study Agreement:

Data to Be Provided by Interconnection Customer with the

Interconnection Facilities Study Agreement

Provide location plan and simplified one-line diagram of the plant and station facilities.

For staged projects, please indicate future generation, distribution circuits, etc.

On the one-line diagram, indicate the generation capacity attached at each metering location. (maximum load on CT/PT).

On the one-line diagram, indicate the location of auxiliary power. (minimum load on CT/PT)

One set of metering is required for each generation connection to the new ring bus or existing T & D Utility station.

Number of generation connections: ________________

Will an alternate source of auxiliary power be available during CT/PT maintenance? Yes _____No_______.

Will a transfer bus on the generation side of the metering require that each meter set be designed for the total plant generation? Yes _________No _________ (Please indicate on the one-line diagram).

What type of control system or PLC will be located at the Generating Facility? ____________________.

What protocol does the control system or PLC use? _____________________ .

Please provide a 7.5-minute quadrangle map of the site. Indicate the plant, station, distribution line, and property lines.

Physical dimensions of the proposed interconnection station: ___________________.

Bus length from generation to interconnection station: ________________________.

Line length from interconnection station to T & D Utility 's Electric Distribution System: ___________________________.

Tower number observed in the field. (Painted on tower leg):* ___________________.

Number of third party easements required for distribution lines:* _______________.*

To be completed in coordination with T & D Utility.

Is the Generating Facility located in T & D Utility 's service area?   Yes _______No _________

If "No," please provide name of local provider:_______________________________________

Please provide the following proposed schedule dates:

Begin construction date: ______________________

Generator step-up transformers receive back feed power date: ______________

Generation testing date: _______________________

Commercial operation date: ____________________