STATE OF MAINE

DRINKING WATER RULE

10-144 CODE OF MAINE RULES

CHAPTER 231

Department of Health and Human Services

Maine Center for Disease Control and Prevention

11 State House Station

Augusta, Maine 04333-0011

December 1, 2025

TABLE OF CONTENTS

SECTION 1: PURPOSE AND DEFINITIONS	1

A.	Purpose	1

B.	Definitions	1

SECTION 2: ADMINISTRATION	9

A.	Application and scope	9

B.	Licensed water operators	9

C.	Departmental laboratory fees	10

D.	Engineering studies/Engineering orders	10

E.	Imminent hazards to public health	10

SECTION 2-A: ANNUAL OPERATION FEES (ALTERNATIVE FUNDING MECHANISM)	12

A.	Fee formulas	12

B.	Formula parameters	13

C.	Fund management	13

D.	Fee revenues to be generated	14

E.	Collection and remittance of fees	14

F.	Records required	14

G.	Failure to remit fees to the Department	15

SECTION 2-B: SAFE DRINKING WATER ADMINISTRATIVE ENFORCEMENT	15

A.	Preconditions for assessment of administrative remedies	15

B.	Notice and issuance, amendment withdrawal of administrative consent orders	16

C.	Notice and issuance, amendment withdrawal of administrative compliance orders	17

D.	Procedures for imposing administrative penalties	18

E.	Assessment of administrative penalties – generally	18

F.	Assessment of administrative penalties – by violation type	18

G.	Assessment of administrative penalties – hearing	20

H.	Assessment of administrative penalties – enforcement	20

I.	Administrative penalty schedule	20

SECTION 3: FACILITIES APPROVAL	25

A.	Review period	25

B.	Siting requirements	25

C.	Plan submission	26

D.	General operations permit	26

E.	Demonstration of capacity	27

F.	Construction standards	28

G.	New sources	30

H.	Existing sources	44

I.	Protective measures	45

J.	Bottled water approval	45

SECTION 4: OPERATION, MAINTENANCE AND DISINFECTION	48

A.	Water pressure	48

B.	Covered reservoirs	48

C.	Flushing	48

D.	Disinfection	48

E.	Separations and crossings of water mains and sewers	48

F.	Cross-connection	49

G.	Hydrants	49

H.	Curb stops	49

I.	Emergency changes	49

J.	Fluoridation	49

K.	Bottled water	52

L.	Sanitary surveys	53

M.	Ongoing water testing requirements for water vending machines	55

N.	Tanks and clearwells	55

SECTION 5: RECORD MAINTENANCE	55

A.	Water analyses	55

B.	Violations	56

C.	Sanitary surveys	56

D.	Variances and exemptions	56

E.	Operational records	56

F.	Assessments required by the revised total coliform rule	56

SECTION 6: REPORTING REQUIREMENTS	57

A.	Any failure of a public water system to comply with the Drinking Water Rule	57

B.	Submittal of water quality samples to a certified laboratory 	57

C.	Analysis reporting to the Department	57

D.	Directly submitting operational reports to the Department	58

E.	Change in ownership	58

F.	Security reports	58

SECTION 7: NATIONAL PRIMARY DRINKING WATER REGULATIONS

(40 CFR Chapter I, SUBCHAPTER D, PART 141)	59

A.	General provisions	59

B.	Maximum contaminant levels	59

C.	Monitoring and analytical requirements	60

D.	Reporting, public notification and record keeping	61

E.	Special regulations including monitoring regulations and prohibition on lead use	62

F.	Maximum contaminant level goals and maximum residual disinfectant level goals	62

G.	National revised primary drinking water regulations: Maximum contaminant levels and maximum residual disinfectant levels.	63

H.	Filtration and disinfection	63

I.	Control of lead and copper	64

J.	Use of non-centralized treatment devices	64

K.	Treatment techniques	64

L.	Disinfectant residuals, disinfectant byproducts and disinfection byproducts precursors	64

M-N [Reserved]	64

O.	Consumer confidence reports	65

P.	Enhanced filtration and disinfection – systems serving 10,000 or more people	65

Q.	Public notification of drinking water violations	65

R [Reserved]	65

S.	Ground water rule	65

T.	Enhanced filtration disinfection – systems serving fewer than 10,000 people	65

U.	Initial distribution systems evaluations	65

V.	Stage 2 disinfection byproducts requirements	66

W.	Enhanced treatment for cryptosporidium	66

X.	[Reserved]	66

Y.	Revised total coliform rule	66

Z.      Per- & poly-fluoroalkyl substances requirements	66

SECTION 8: NATIONAL PRIMARY DRINKING WATER REGULATIONS-

IMPLEMENTATION (40 CFR-PART 142)	67

A.	General provisions	67

B.	Primary enforcement responsibility	67

C.	Review of State-issued variances and exemptions	68

D.	Federal enforcement	69

E.	Variances issued by the administrator under Section 1415 (a) of the Act	69

F.	Exemptions issued by the administrator	70

G.	Identification of best technology, treatment techniques or other means generally

available	71

H.	Indian Tribes	71

I.	Administrator’s review of State decisions that implement criteria under which filtration

is required	72

J.	[Reserved]	72

K.	Variances for small systems	72

SECTION 9: NATIONAL SECONDARY DRINKING WATER REGULATIONS

(40 CFR CHAPTER I, SUBPART D, 143)	74

A.	General provisions	74

SECTION 10: LABORATORY CERTIFICATION	74

SECTION 11: RISK AND RESILIENCE ASSESSMENTS, EMERGENCY RESPONSE PLANS, CYBERSECURITY AND NOTIFICATION PROCEDURES FOR PUBLIC WATER

SYSTEMS	75

A.	Emergency situations	75

B.	Risk and resilience assessments	75

C.	Emergency response plans	76

D.	Cybersecurity	77

E.	Security breaches and emergency notification requirements	77

STATUTORY AUTHORITY	77

APPENDIX A: Analyte monitoring requirements for new well approval and routine compliance

monitoring	79

APPENDIX B: NPDWR Contaminants MCL and MCLG Table	85

SECTION 1: PURPOSE AND DEFINITIONS

A.	Purpose. This rule governs the requirements for public water systems supplying drinking water to residents and visitors within the State of Maine for protection of public health, in accordance with Title 22 MRS, Chapter 601. This rule identifies drinking water contaminants which may have health effects, specifies an acceptable maximum contaminant level or one or more treatment techniques for each, and establishes criteria and procedures to ensure compliance through proper operation and maintenance, quality control, and testing procedures. In addition, this rule provides the Department’s enforcement remedies in response to violations of this rule, as well as water quality requirements for bottled water facilities and water vending machines.

B.	Definitions. The definitions in this rule supplement the definitions in the applicable statutes.

1.	Act means the Public Health Service Act, as amended by the Safe Drinking Water Act, Public Law 93-523.

2.	Action level means the concentration of lead or copper in water specified in 40 CFR §141.80(c), which determines, in some cases, the treatment requirements contained in Subpart I of §141.80(c) that a water system is required to complete.

3.	Administrative compliance order means an administrative order that is issued by the Commissioner against a public water system found to be in violation of State drinking water laws, regulations or rules.

4.	Administrative consent order means an order issued by the Commissioner pursuant to a bilateral agreement between the Commissioner and a public water system found to be in violation of State drinking water laws, regulations or rules.

5.	Administrative penalty means a fine imposed by the Commissioner against a public water system found to be in violation of State drinking water laws, regulations or rules.

6.	Administrative remedy means an administrative compliance order, an administrative consent order or an administrative penalty.

7.	APA means The Maine Administrative Procedure Act, Title 5 MRS Chapter 375.

8.	Available means on site or able to be contacted as needed to initiate the appropriate action in timely manner based on the system size, complexity, and source water quality.

9.	AWWA : means the American Water Works Association.

10.	Best available technology (BAT) means the best technology, treatment techniques, or other means that the Administrator finds, after examination for efficacy under field conditions and not solely under laboratory conditions, are available (taking cost into consideration). For the purposes of setting MCLs for synthetic organic chemicals, any BAT must be at least as effective as granular activated carbon.

11.	Bottled water means water intended for human consumption and placed in sanitary bottles, packages or other containers and intended for sale to the public.

12.	Bottler size factor means the category assigned to in-state bottled water companies to determine annual fees assessed by the Department.

13.	Capacity means the technical, financial and managerial resources of a water system necessary to enable the system to consistently provide safe drinking water for its users.

a.	Technical capacity means the physical infrastructure of the water system, including but not limited to source water adequacy, infrastructure adequacy (including wells, source water intakes, and collection, treatment, storage and distribution), and the ability of system personnel to implement the requisite technical knowledge necessary to operate the system to consistently provide safe drinking water.

b.	Financial capacity means the financial resources of the water system, including but not limited to revenue sufficiency, credit worthiness and fiscal management and controls.

c.	Managerial capacity means the management structure of the water system, including but not limited to ownership accountability, staffing and organization, and the effectiveness of interactions of system personnel with consumers, regulators and other entities, and the awareness of system personnel of available external resources, such as technical and financial assistance.

14.	Certified laboratory means a laboratory accredited by the Maine Department of Health and Human Services, pursuant to 22 MRS §567.

15.	Clean compliance history refers to the Revised Total Coliform Rule, referenced in Section 7(Y) of this rule. A public water system with this status demonstrates a record of no MCL violations within the last 12 months; no monitoring violations within the last 12 months; and no coliform treatment technique trigger exceedances or treatment technique violations within the last 12 months.

16.	Code of Federal Regulations (CFR) means the compilations of the general and permanent rules of the executive departments and agencies of the federal government, published in the Federal Register and then annually by the U.S. Government Printing Office. Sections of the CFR that this Rule specifically refers to and incorporates by reference are various sections of Title 40 CFR Parts 141-143, which include the National Primary Drinking Water Regulations. In this rule, any citations incorporating sections of the CFR by reference, refers to the edition published in July 2024. Copies of the referenced sections of the CFR are available upon request from the Department at (207) 287-2070, and are also accessible on line at the following website links:

- Part 141:

https://www.ecfr.gov/cgi-bin/text-idx?tpl=/ecfrbrowse/Title40/40cfr141_main_02.tpl

- Part 142:

https://www.ecfr.gov/cgi-bin/text-idx?tpl=/ecfrbrowse/Title40/40cfr142_main_02.tpl https://www.ecfr.gov/cgi-bin/text-idx?tpl=/ecfrbrowse/Title40/40cfr142_main_02.tpl

- Part 143:

https://www.ecfr.gov/cgi-bin/text-idx?tpl=/ecfrbrowse/Title40/40cfr143_main_02.tpl

17.	  Commission means the Maine Public Drinking Water Commission.

18.	Commissioner means the Commissioner of the Maine Department of Health and Human Services.

19.	Common scheme of development means a plan or process of development which takes place on contiguous or non-contiguous parcels or lots in the same immediate vicinity and exhibits characteristics of a unified approach, method or effect, such as unified ownership, management or supervision, sharing of common equipment or labor, or common financing.

20.	Community water system means a public water system that serves at least 15 service connections used by year-round residents or regularly serves at least 25 year-round residents.

21.	Consecutive public water system means a public water system that buys or otherwise receives at least some of its finished water from another public water system. Public water systems that are interconnected only for emergencies are not considered consecutive public water systems.

22.	Contaminant means any physical, chemical, biological or radiological substance or matter in water, as specified by the National Primary Drinking Water Standards of the Safe Drinking Water Act, 40 CFR § 141.2.

23.	Conventional filtration treatment means a series of processes including coagulation, flocculation, sedimentation, and filtration resulting in substantial particulate removal.

24.	Department means the Department of Health and Human Services, Maine Center for Disease Control and Prevention.

25.	Designated operator in responsible charge (or Designated operator or DO) means an individual who is appropriately licensed for treatment and distribution classification of the public water system. The operator’s licensure must meet the applicable classification of the public water system’s treatment or distribution system.

26.	Disinfection means the application of any oxidant, including, but not limited to chlorine, chlorine dioxide, chloramines, and ozone, that is added to water in any part of the treatment or distribution process and is intended to kill or inactivate pathogenic microorganisms. Disinfection treatment includes ultraviolet (UV) treatment.

27.	Disinfection profile means a summary of daily Giardia lamblia inactivation through the treatment plant. The procedure for developing a disinfection profile is contained in 40 CFR §141.172.

28.	Division means the Division of Environmental and Community Health within the Maine Center for Disease Control and Prevention, Department of Health and Human Services.

29.	Engineering study means a technical evaluation by a licensed professional of a public water system’s source, treatment, pumpage, distribution and/or storage, to identify deficiencies which limit or prohibit the ability of a public water system to reliably provide water of acceptable quality and/or quantity. Licensed professionals include engineers, well drillers, electricians, plumbers, water operators, geologists, and other licensed professionals approved by the Department. The engineering study also recommends a course of action to implement improvements as needed.

30.        Fluoridation means the addition of a chemical to increase the concentration of fluoride ion in drinking water to a predetermined optimum range to reduce the incidence of dental caries (tooth decay).

31.	Fund means the Public Drinking Water Fund or Maine Drinking Water Fund at 22 MRS § 2610.

32.	Gross alpha particle activity means the total radioactivity due to alpha particle emission as inferred from measurements on a dry sample.

33.	Ground water means water underground in the soil or in pores and crevices in rock.

34.	Ground water under the direct influence of surface water means any water beneath the surface of the ground with significant occurrence of insects or other macro-organisms, algae, or large-diameter pathogens such as Giardia lamblia or (for subpart H systems serving at least 10,000 people only) Cryptosporidium, or significant and relatively rapid shifts in water characteristics such as turbidity, temperature, conductivity, or pH which closely correlate to climatological or surface water conditions. Direct influence must be determined for individual sources in accordance with criteria established by the Department. The Department determination of direct influence may be based on site-specific measurements of water quality and/or documentation of well construction characteristics and geology with field evaluation.

35.	Hearing means an administrative hearing conducted by the Administrative Hearings Unit within the Department.

36.	Hearing officer means an impartial and independent person designated by the Department to conduct hearings.

37.	Hydrofracturing means a process of applying hydraulic pressure on the bedrock surrounding the drilled well for the purpose of increasing the yield of the well.

38.	ISL means an in-state large bottled water company supplying more than 20 million gallons of bottled water per year.

39.	ISM means an in-state medium bottled water company supplying more than 250,000 gallons but less than 20 million gallons of bottled water per year.

40.	ISS means an in-state small bottled water company supplying less than or equal to 250,000 gallons of bottled water per year.

41.	Laboratory sampling form means  the form that provides documentation as to when, where and by whom water samples were collected.

42.	Level 1 assessment means an evaluation of a public water system under the Revised Total Coliform Rule, 40 CFR §§ 851-861, to identify the possible presence of sanitary defects, defects in distribution system coliform monitoring practices, and (when possible) the likely reason that the public water system triggered the assessment.

43.	Level 2 assessment means an evaluation of a public water system that is required under the Revised Total Coliform Rule 40 CFR §§ 851-861, to identify the possible presence of sanitary defects, defects in distribution system coliform monitoring practices, and (when possible) the likely reason that the system triggered the assessment. A level 2 assessment provides a more detailed examination of the public water system (including its monitoring and operational practices) than a level 1 assessment, through the use of more comprehensive investigation and review of available information, additional internal and external resources, and other relevant practices.

44.	Maximum contaminant level (MCL) means the maximum permissible level of a contaminant in water which is delivered to the free flowing outlet of the ultimate user of a public water system, except in the case of turbidity where the maximum permissible level is measured at the point of entry to the distribution system.

45.	Natural fluoride level means the concentration of fluoride that is present in the water source from naturally occurring fluoride.

46.	New public water system source means any newly constructed well, intake, or other structure intended as a supply of water for a public water system. Any existing well, intake or other structure intended for use as a source of water for a public water system that has not been actively regulated by the Department in the previous five years will be considered a new source. All new sources of water intended for use by a public water system will be subject to the new source approval provisions of this rule.

47.	Notice of non-compliance means a formal written complaint or a notice of violation of State drinking water laws, regulations, or rules.

48.	NSF/ANSI means the NSF International and the American National Standards Institute. The American National Standards Institute acts as a certifying agency and determines which laboratories may certify these standards.

49.	Operating shift means that period of time during which operator decisions that affect public health are necessary for proper operation of the system.

# 50.	Outstanding performance means a  time frame covered by the preceding two sanitary surveys, during which the system did not have any significant deficiencies identified, did not have any failure-to-monitor violations and met all required testing parameters.

51.	Per-machine rate means the rate used to determine annual fees assessed by the Department for water vending machines.

52.	Person means an individual, association, partnership, company, public or private corporation, political subdivision or agency of the State, Department, agency or instrumentality of the United States or any other legal entity.

53.	Picocurie (pCi) means that quantity of radioactive material producing 2.22 nuclear transformations per minute.

54.	Primacy means the federally delegated primary enforcement authority to adopt, implement and enforce federally mandated drinking water standards promulgated pursuant to the federal Safe Drinking Water Act as amended.

55.	Program means the Maine Public Drinking Water Program.

56.	Public water system means any publicly or privately owned system of pipes or other constructed conveyances, structures and facilities through which water is obtained or sold, furnished or distributed to the public for human consumption, if such a system has at least 15 service connections, regularly serves an average of at least 25 individuals daily at least 60 days out of the year or bottles water for sale. Any publicly or privately owned system that only stores and distributes water, without treating or collecting it; obtains all its water from, but is not owned or operated by, a public water system; and does not sell water or bottled water to any person, is not a public water system. The term public water system includes any collection, treatment, storage or distribution pipes or other constructed conveyances, structures or facilities under a common scheme of development within the control of the water supplier and used primarily in connection with such a system, and any collection or pretreatment storage facilities not under that control that are used primarily in connection with such a system. The system does not include the portion of service pipe owned and maintained by a customer of the public water system. Public water systems include the following types:

a.	Community water system means a public water system which serves at least 15 service connections used by year-round residents or regularly serves at least 25 year-round residents.

b.	Non-Community Water System means a public water system that is not a community water system. There are two types of non-community water systems defined below:

i.	Non-transient, non-community water systems means a non-community water system that serves at least 25 of the same persons for 6 months or more per year and may include, but is not limited to, a school, factory, industrial park or office building, and

ii.	Transient non-community water systems means a non-community water system that serves at least 25 persons, but not necessarily the same persons, for at least 60 days per year and may include, but is not limited to, a highway rest stop, seasonal or year-round restaurant, seasonal or year-round motel, golf course, park or campground.  A bottled water company is a transient, non community water system.

This definition contains further clarification of the public water system definition in Maine’s Water for Human Consumption statute, 22 MRS §2601(8), and the National Primary Drinking Water Regulations, 40 CFR § 141.2.

57.	Raw source water means water drawn directly from a spring, drilled well, or dug well prior to disinfection, filtration, storage or other treatment processes.

58.	Responsible charge means having been designated by the owner to be the licensed operator(s) who makes decisions regarding the daily operational activities of a public water system, water treatment facility and/or distribution system, that will directly impact the quality and/or quantity of drinking water.

59.	Revised total coliform rule means 40 CFR Parts 851-861of the National Primary Drinking Water Regulations and incorporated by reference within rule that establishes a maximum contaminant level for E. coli and uses total coliform and E. coli to initiate a find-and-fix approach to address fecal contamination that could enter a public water system by requiring public water systems to perform level 1 and level 2 assessments, to identify sanitary defects and take action to correct them.

60.	Sample or water sample means an amount of  raw (untreated) source water or finished (treated) drinking water that is examined for the presence of a contaminant.

61.	Sanitary defect means a particular condition that could provide a pathway of entry for microbial contamination into the distribution system or that is indicative of a failure or imminent failure in a sanitary or treatment barrier that is already in place.

62.	Sanitary seal well cap means a well cap sealed with a gasket between the cap and the well casing. The connection between the well cap and the electrical conduit is tight, to prevent insects or other vermin from entering the well.

63.	Sanitary survey means the Department’s on-site inspection of the water source, facilities, and treatment equipment, with a focus on the operation and maintenance of a public water system for the purpose of evaluating the protection of the source; and the adequacy of such source, facilities, equipment, operation and maintenance for producing and distributing safe drinking water. The Department performs sanitary surveys for community public water systems every three years, and for non-community public water systems every five years, except for public water systems with a surface water source, or with a source of groundwater under the direct influence of surface water, as defined in Section 1(B)(34) of this rule, and bottled water facilities, which are performed every three years. Bottled water sanitary surveys entail the inspection of any source water, operations and treatment equipment from the source, leading up to the bottling process.

# 64.	Seasonal system means a non-community public water system that is not operated as a public water system on a year-round basis and starts up and shuts down at the beginning and end of each operating season.

# 65.	Secondary maximum contaminant level (SMCL) means the maximum recommended level of a contaminant in water which is delivered to the free flowing outlet of the ultimate user of the public water system. The SMCLs are non-mandatory limits established as guidelines to assist public water systems in managing their drinking water for aesthetic considerations, such as taste, color and odor. The contaminants with established SMCLs are not considered to present a risk to human health at the SMCL.

# 66.	Significant deficiency means any defect in a system’s design, operation, maintenance or administration, as well as any failure or malfunction of any system component, that causes, or has the potential to cause, an unacceptable risk to health or that could affect the reliable delivery of safe drinking water.

67.	Spring water means water derived from an underground formation from which water flows naturally to the surface of the earth. Spring water must comply with the U.S. E.P.A. National Primary and Secondary Drinking Water Standards, 40 CFR parts 141-143 and U.S. Food and Drug Administration Regulations at 21 CFR §165.110 (a)(vi). Spring water must be collected only at the spring or through a borehole tapping the underground formation feeding the spring. There must be a natural force causing the water to flow to the surface through a natural orifice. The location of the spring must be identified, and such identification must be maintained in the plant’s records. Spring water collected with the use of an external force must be from the same underground stratum as the spring, as shown by a measurable hydraulic connection, using a hydrogeologically valid method between the bore hole and the natural spring, and must exhibit all of the physical properties before treatment, and be of the same composition and quality as the water that flows naturally to the surface of the earth. A water chemistry comparison is typically performed by plotting cations and anions for both the spring and borehole on a Piper Diagram. If spring water is collected with the use of an external force, water must continue to flow naturally to the surface of the earth through the spring’s natural orifice. Upon request by the Department, bottled water plants must demonstrate, by using a hydrogeologically valid method, that an appropriate hydraulic connection exists between the natural orifice of the spring and the borehole. Such a demonstration must be submitted by a hydrogeologist certified to perform this type of work in the State of Maine.

68.	Surface water means all water naturally open to the atmosphere (rivers, lakes, reservoirs, streams, impoundments, seas, estuaries, etc.) and all springs, wells or other collectors which are directly influenced by surface water.

69.	Supplier of water; water supplier; supplier means any person who controls, owns, or generally manages a public water system.

70.	System means a public water system.

71.	System design capacity for authorized community water systems withdrawing from surface waters means the amount of water that is available for community water system purposes expressed as annual withdrawal in total gallons per year taking into consideration actual documented annual withdrawal, and the investments in and limits of the existing system infrastructure, that provides a safe and dependable supply of water for public use. Existing system infrastructure includes water treatment and distribution facilities and other necessary structures that determine how much water can be safely and dependably supplied that is present or in the process of being acquired such as through an investment bond, contractual agreement, or purchase order as of the effective date of the Department of Environmental Protection’s In-stream Flows and Lake and Pond Water Levels Rule (06-096 CMR Chapter 587).

72.	Theoretical fluoride concentration means the calculated concentration of fluoride ion in a distribution system which includes the theoretical fluoride dose plus the natural fluoride level.

73.	Theoretical fluoride dose means the calculated dose of fluoride ion added to a drinking water source or supply.

74.	Violation means noncompliance with State drinking water laws, regulations and rules regardless of whether that noncompliance is intentional, negligent or otherwise.

75.	Water vending machines means any self-service device located in a retail store, which is a public water system or is served by a public water system, which, upon insertion of coins or tokens, dispenses unit servings of water into a customer’s container.

# SECTION 2: ADMINISTRATION

## A.	Application and Scope

The provisions of this rule apply to all public water systems (PWS), unless specifically noted.

## B.	Licensed Water Operators

1.	Owners of all community and non-transient non-community water systems must place the direct supervision of their water system, including each treatment facility and/or distribution system, under the responsible charge of an operator holding a valid license with classification equal to or greater than the classification of the treatment facility and/or distribution system.

2.	Owners of all public water systems that use surface water as a source must place the direct supervision of their water system, including each treatment facility and/or distribution system, under the responsible charge of an operator holding a valid license equal to, or greater than, the classification of the treatment facility and/or distribution system.

3.	The operator in responsible charge must ensure that adequate operational and emergency response procedures are in place to enable licensed operating personnel to make appropriate process control decisions about water quality and quantity.

4.	All operating personnel making process control system integrity decisions about water quality or quantity that affect public health must be licensed.

5.	A designated licensed operator must be available for each operating shift.

6.	Transient non-community water systems serving ground water are generally not required to employ licensed operators. However, these water systems must employ or designate individuals responsible for their operation, who are responsible for proper record-keeping, treatment, maintenance, and sample collection, as required by this rule. If the Department finds that such transient water systems demonstrate a lack of capacity (as described in Section 3(E) of this rule) or pose an imminent hazard to public health (as described in Section 2(E) of this rule), then the Department may require that the water system engage a licensed water operator holding an appropriate license for the system classification.

7.	Whenever a licensed water operator is required, that operator must maintain their licensure and must comply with this rule.

a.	If the Department finds that a water operator is not complying with this rule, then the Department may require that the water system obtain a different licensed operator.

b.	A public water system required to have a licensed operator may not operate without a licensed operator for more than five business days.

c.	The public water system must submit a new signed designated operator form to the Department within five days of learning of the previous operator’s departure.

## C.	Departmental Laboratory Fees

1.	The Department will charge a fee for any examination, testing or analysis required under this rule and performed in the Department of Health and Human Services, Maine CDC, Health and Environmental Testing Laboratory. Such fees will be established and reviewed in accordance with the Schedule of Charges of the Diagnostic Laboratory of the Department of Health and Human Services (10-144 CMR Chapter 257).

2.	Any person required under this rule to submit samples of water to the Department for analysis is required to pay the shipping charges thereon.

## D.	Engineering Studies/Engineering Orders

1.	The Department is authorized to order a public water system to conduct engineering studies to correct deficiencies or violations to the Safe Drinking Water Act, or this rule.

2.	The Department is authorized to order that any or all of the recommendations in the study be carried out.

3.	The Department is authorized to issue an Engineering Order when a public water system has significant water system deficiencies or fails to meet deadlines to resolve water system deficiencies.

## E.	Imminent Hazards to Public Health

1.	Pursuant to 22 MRS §2617, the Department is authorized to issue orders to any person to comply with the requirements of this rule and is further authorized to petition the courts to compel compliance with such orders.

2.	Pursuant to 22 MRS §2614, upon receipt of information that there is an imminent hazard to health due  to the actual or threatened existence of contaminants in a public water system, or if for other reasons, the Department may take such actions, including, but not limited to, issuing necessary do not drink orders, do not use orders or boil water orders, or commencing court action, as it deems necessary to protect the public health.

3.	Pursuant to 22 MRS §2614(3), the Department may initiate boil water order procedures, upon receipt of information that there is an imminent hazard to public health due to the actual or threatened existence of biological contaminants, as indicated by the presence of pathogenic microorganisms or the presence of indicator organisms that indicate the potential presence of pathogenic microorganisms, in a public water system. Boil water order procedures may also be initiated by the Department, when, in the judgment of the Department, such a condition exists, or is likely to exist, in a public water system and will result in a serious risk to public health. The Department will immediately notify the public water system of the determination. Upon notification by the Department of the Boil Water Order, the public water system must immediately institute the Boil Water Order system-wide, or as otherwise directed by the Department until such time as the Department makes the determination that the Boil Water Order may be lifted.

4.	Boil water order procedures

a.	The Department will provide the appropriate Boil Water Order language to the owner, manager, or other responsible individual by telephone, electronic notification, FAX or in person, for immediate distribution to customers.

b.	If the Department is unable to contact an appropriate person, then the Department's field staff may distribute handbills to customers.

c.	Nothing in these Boil Water Order procedures absolves the supplier of water from providing appropriate public notification to their customers.

d.	When a public water system is issued a Boil Water Order by the Department, that water system shall appropriately notify customers within 24 hours of its issuance. Notification of the Boil Water Order must be accomplished by one or more of the following methods: broadcast media, such as television or radio; posting throughout the service area affected in conspicuous locations; hand delivery to consumers; or by another method approved by the Department. Department-approved methods may include social media, email, or any other method(s) used designed to effectively reach all consumers affected by the Boil Water Order. The following language must be included in all Boil Water Order notices distributed by the system:

Due to the possibility of unsafe water, public water system users are directed to boil all water for at least one minute at a rolling boil before drinking, making ice cubes, washing foods, brushing teeth or engaging in any other activity involving the consumption of water. The Order must remain in effect until further notice.

Questions regarding this notice may be directed to the Public Water System at:

Fill-in: Name of Contact Person

Name of System

Telephone # or to the Maine C.D.C. Drinking Water Program at (207) 287-2070.”

e.	The Department may lift the Boil Water Order if it determines that the imminent hazard to public health has been remedied. Prior to lifting the Boil Water Order, the Department will collect, or require the public water system to collect, the appropriate number of bacteria samples:

The required number of samples collected to lift a Boil Order must reflect population and area impacted, in accordance with the requirement of the Total Coliform Rule and the Revised Total Coliform Rule in Section 7, but in no case may be less than three samples.

All E. coli/ total coliform/fecal coliform results must be negative in order for the Department to lift the Boil Water Order.

# SECTION 2-A ANNUAL OPERATION FEES

# (ALTERNATIVE FUNDING MECHANISM)

Pursuant to 22 MRS §2660-E, an annual operation fee may be imposed upon each public water system (PWS) in the State of Maine to assist the Department with retaining primacy with EPA. The Department continues to establish fee formulas in this section in accordance with 22 MRS §2660-E (1), with consultation and  advice from the Maine Public Drinking Water Commission (the Commission) in determining and setting the formulas below. These annual Department fees are enacted, pursuant to 22 MRS §2660-E, and the Department will use revenues generated from collection of these fees  for the purpose of retaining primacy, including the funding of Department positions as stated below.

## A.	Fee Formulas

1.	Pursuant to 22 MRS §2660-E (Maine’s Water for Human Consumption Act), the following fee formula is established for all public water systems, except bottled water and water vending machines:

a.	The annual fee is equal to the base fee plus the per capita rate multiplied by the population capacity minus the exempt population.

- Annual fee = base fee + ((per capita rate) x (population capacity) – (exempt population.))

c.	The base fee assessed will not exceed $75.

d.	The per capita fee for public water systems serving over 100 customers will not exceed $1.00.

2.	Pursuant to 22 MRS §2660-E (Maine’s Water for Human Consumption Act), the following fee formulas are established for bottled water facilities and treated water vending machines:

a.	The fee schedule for in-State water bottlers will be based on gallons produced. (Bottler size factor multiplied by fee rate per bottler size). The Drinking Water Commission and the Department will set the fee rate per bottler size factor annually.

b.	The fee for bottled water facilities producing less than or equal to 250,000 gallons per year is $105.00

c.	The fee for bottled water facilities serving more than 250,000 gallons and less than 20 million gallons per year is $300.

d.	The fee for bottled water facilities serving more than 20 million gallons per year is $3,900.

e.	The fee schedule for treated water vending machines will be calculated at a rate of $10 per machine, with a minimum fee of $50 per vendor and not to exceed a maximum of $250. (Base fee + (Per-machine rate multiplied by the number of machines)).

f.	Production reports are subject to annual verification by the Department. Failure to comply may result in an assessment of the maximum bottled water fee.

B.	Formula Parameters

1.	The following parameters will be used to determine and calculate the annual fee for regulated public water systems:

a.	The minimum fee will be equal to the base fee;

b.	The base fee will be no more than $75 per year per public water system (22 MRS §2660-E);

- The Commission and the Department will establish the per capita rate annually.

d.	The population capacity will be based on, but not limited to, the population served, service connections, volume of water pumped or available seats, campsites, rooms or lots, and may include a fixed or graduated fee formula or combinations of the fee formulas; and

e.	An exempt population may be determined to be part of the annual fee and subtracted from the population capacity, as determined by the Commission and the Department annually, pursuant to 22 MRS §2613.

2.	The following parameters will be used to determine and calculate the bottled water and treated water vending machines annual fee for regulated public water systems:

a.	All in-State bottlers must submit gallon production reports for the year ending December 31, and such annual reports are due to the Department no later than March 1st.

- The production report, which will provide the number of gallons produced for the sale of bottled water, will be used to calculate the annual fee.

c.	Fees collected under this section cover a one-year period beginning July 1 and will coincide with the State fiscal year.

## C.	Fund Management

1.	The Fund will be managed within the following parameters:

a.	The Public Drinking Water Fund is established as an interest-bearing dedicated revenue account;

b.	All interest earned by the account becomes part of the fund;

c.	All fees collected by the Department under this rule must be deposited into the fund;

d.	Any balance remaining in the fund at the end of the fiscal year does not lapse but is carried forward into subsequent fiscal years; and

e.	The Department may use the fund only to support the cost incurred in managing the Fund, including the cost of salaries, benefits, travel, education, technical assistance, capital equipment and other allowable expenses.

2.	Collection and disposition of fees pursuant to 22 MRS §2660-F

- All public water systems must pay an annual fee.

- Fees collected under this section cover a one-year period beginning July 1 and will coincide with the State fiscal year;

- Fees collected under this section are State fees;

- Fees must be collected by each public water system in monthly, quarterly, or annual increments; and

- The Department will establish schedules for the collection and transfer of fees to the State with the advice of the Commissioner.

## D.	Fee Revenues to be Generated. The fee structure must be sufficient to generate funds to support no more than 10 positions for a full year.

## E.	Collection and Remittance of Fees

1.	Any legal entity assessed a total fee of $500 or more may exercise the option of remitting the assessed fee on a quarterly basis. Fees so remitted will be due and payable July 1, October 1, January 1, and April 1. Legal entities opting to remit on a quarterly basis must remit at least 25 percent of the total assessment each quarter. Any public water system with invoices 30 days past due constitutes a violation, as described in Section 2-A (G) of this rule.

2.	Any legal entity assessed a total fee of $500 or more that opts not to pay fees on a quarterly basis must pay fees to the Department annually. Such fees will be due and payable upon invoice receipt each calendar year. Any public water system with invoices 30 days past due constitutes a violation, as described in Section 2-A (G) of this rule.

3.	Any legal entity assessed a total fee of less than $500 must remit the assessed fee on an annual basis. Fees remitted on an annual basis must be due and payable upon invoice receipt each calendar year. Any public water system with invoices 30 days past due constitutes a violation, as described in Section 2-A (G) of this rule.

4.	Fee payments must be addressed to “Treasurer, State of Maine” and, pursuant to 22 MRS §2660-F, will be deposited by the Department into the Public Drinking Water Fund.

## F.	Records Required

1.	Records documenting the collection and transfer of fees required in this rule must be retained by the owner or other duly authorized person. The records must be kept in-State and on-site of the public water system for a period of at least five years. If it is not possible to keep the records on-site, then the records must be kept such that an appropriate person from the Department may inspect such records upon request. Further, the records must be transferred to the new owner with the sale of the public water system.

2.	Records documenting the collection and transfer of fee payments, as required in this rule, must be made readily available by the owner or other duly authorized person, for inspection by appropriate authorities at all times during normal business hours.

3.	The Department will keep records documenting the collection and transfer of all fees assessed for at least five years.

# G.	Failure to Remit Fees to the Department. Failure to pay annual fees to the Department in a timely manner constitutes a violation of this rule. The Department determines any delay or failure to remit payment after 30 days from the payment deadlines set in Section 2-A(E)(1)-(3) to be a violation of Section 2-A. Any violation of this rule, (including failure to pay annual fees or failure to meet the deadline of a Notice of Noncompliance), may result in the Department seeking relief in accordance with Section 2-B of this rule.

# SECTION 2-B: SAFE DRINKING WATER ADMINISTRATIVE ENFORCEMENT

The Department may seek and impose administrative remedies for any noncompliance with the State drinking water laws, regulations and rules. In seeking and imposing enforcement actions, the Department may pursue any combination of administrative and judicial remedies depending upon the circumstances and gravity of each case and provided that the Department follows the procedures established by statute and further established by this rule.

## A.	Preconditions for Assessment of Administrative Remedies

1.	An administrative remedy may only be administered for a violation or a failure to comply that, at the time it occurred, constituted noncompliance with statutes or rules under the jurisdiction of the Department's Drinking Water Program:

a.	Which was then in effect; and

b.	To which the person was then subject; and

c.	To which this rule apply.

2.	The imposition of administrative remedies will not be deemed in any way to extend any deadline for compliance.

3.	The Department will issue a notice of non-compliance as part of the administrative remedy process, unless exempt under 22 MRS §2620-B. A notice of non-compliance will be issued by the Department within 30 days after a violation is identified under 22 MRS §2619 and contains the following information:

a.	Identification of the violation(s);

b.	A compliance deadline to resolve the violation; and

c.	The possible consequences of continued noncompliance.

## B.	Notice and Issuance, Amendment and Withdrawal of Administrative Consent Orders

1.	The Department may propose an administrative consent order to the owner of a public water system after a notice of non-compliance has been issued in accordance with 22 MRS §2619(2), and after the public water system has failed to resolve any violation(s) cited in the notice of non-compliance by the notice of non-compliance deadline. Administrative consent orders are issued in accordance with the following:

a.	The Department's proposal of an administrative consent order initiates the Department's effort to negotiate in good faith;

b.	The proposed administrative consent order is sent via certified mail and service will be effective the date of receipt of the certified mail. If the certified mail is not received or claimed by the public water system supplier, then the Department will send the proposed administrative consent order by first-class US mail

c.	The owner or representative of the public water system is responsible for contacting the Department to accept the offer to negotiate in good faith. If the owner or other representative fails to contact the Department within 10 calendar days, and if the Department has received no evidence that the owner or representative is willing to negotiate in good faith, then the Department is deemed to have fulfilled its good faith effort requirement;

d.	The administrative consent order will state with reasonable specificity the rule or regulation that the public water system violated, specify a reasonable time frame for compliance, and clearly specify the terms under which the Department may cease to negotiate in good faith and therefore revoke the offer;

e.	Generally, the Department will be deemed to have fulfilled its obligation to negotiate in good faith if the public water system owner or representative either failed to contact the Department within ten days of receipt of the administrative consent order, or failed to reach an agreement with respect to the proposed administrative consent order within 60 calendar days from the date of receipt of notice.

i.	If the public water system incurred only monitoring/reporting violations, public notification violations or failure to pay annual fee violations, then the Department and public water system owner must finalize the administrative consent order within 30 days of receipt. If they do not finalize the order, then the Department is deemed to have fulfilled its obligation to negotiate a settlement in good faith; and

ii	If the public water system incurred any Type I violations listed in Section 2-B(I)(1), then the Department and public water system owner or representative must finalize the administrative consent order within 60 days of receipt. If they do not finalize the order, then the Department is deemed to have fulfilled its obligation to negotiate a settlement in good faith.

f.	If the Department has fulfilled its obligation to negotiate in good faith as specified in Section 2-B(1)(f) above, then the Department may revoke its offer to enter into an administrative consent order.

2.	The administrative consent order will become final on the date of the last signatory. The Department will be the last signatory.

3.	The amendment of an administrative consent order may only occur with the consent of both parties to the agreement. Any requests to amend the agreement must be placed in writing.

## C.	Notice and Issuance, Amendment and Withdrawal of Administrative Compliance Orders

1.	The Department may issue an administrative compliance order pursuant to 22 MRS §2619(3), as specified below, provided that the Department has issued a notice of non-compliance, the water system has failed to resolve the violations cited in the notice of non-compliance by the deadline, and the Department has fulfilled its good faith obligation or has made the determination that the violation creates a serious risk to public health as specified at 22 MRS §§2619(2) and 2620-B.

a.	The administrative compliance order may be issued by the Department and sent to the owner of the public water system;

b.	The administrative compliance order will be sent via certified mail. and service is effective on the date of receipt of the certified mail; and

c.	The administrative compliance order will state with reasonable specificity the nature of the rule or regulation that the public water system has violated, specify a reasonable time frame for returning to compliance, provide the owner or representative of the public water system with an opportunity to request a hearing within 30 calendar days of receipt of notice and specify a penalty that may be assessed if the PWS fails to comply with the order.

2.	Requests for Administrative Hearings

a.	Administrative hearings are conducted by the State of Maine Department of Health and Human Services Division of Administrative Hearings in accordance with the Maine Administrative Procedure Act (5 MRS Ch. 375) and the Administrative Hearings Regulations (10-144 CMR Ch.1). The public water system supplier must request a hearing in writing and direct this request to the Department; and

b.	After the hearing officer's decision is issued, it is deemed to be the Department's final agency action and is binding on the Department.  A party aggrieved by the decision has a right to judicial review under the Maine Rules of Civil Procedure, Rule 80C.

3.	The administrative compliance order may only be amended by the Department. If a public water system desires an extension of time to the administrative compliance order, then the system must place a request in writing to the Department prior to the passage of the deadline. The written request for an extension of time must clearly specify actions taken by the system to attempt to prevent non-compliance with a deadline, establish that the delay in compliance is beyond the control of the water system, and the length of time needed for compliance. Otherwise, the passage of the deadline of an administrative compliance order constitutes non-compliance with the administrative compliance order and triggers the notice of penalty assessment of an administrative fine.

4.	If the Department determines that a violation creates a serious risk to public health, then the Department is exempt from issuing a Notice of Non-compliance and from offering to negotiate an administrative consent order in good faith. In this case, the Department may immediately issue an administrative compliance order.

a.	The term serious risk to public health may include, but is not limited to, a maximum contaminant level (MCL) or treatment technique violation.

## D.	Procedures for Imposing Administrative Penalties

1.	In the case of a violation of a requirement of a statute, rule, or order for which the applicable statute authorizes an administrative penalty and which imposes an affirmative duty on a person, the person upon whom the duty is imposed will be required to pay the administrative penalty, in accordance with 22 MRS §2619 (4).

2.	In the case of a violation of this rule, or an administrative order for which the Department is authorized to assess an administrative penalty, and which prohibits one or more specified acts, any person who commits the act(s) will be subject to the administrative penalty.

## E.	Assessment of Administrative Penalties – Generally

1.	An administrative penalty will be assessed via a notice of penalty assessment. An administrative penalty may be assessed as part of an administrative compliance order and is assessed when a public water system violates an administrative compliance order.

2.	The earliest that an administrative penalty may be assessed is at the date good faith efforts cease and the Department has failed to enter into an administrative consent order or on the date that a public water system fails to comply with an administrative compliance order.

- In the event that a penalty is not specified for a particular violation, the Department may assess a penalty for the violation that reflects the type of violation. The penalty assessed may be no greater than $750 per violation per day except that for public water systems serving more than 10,000 people, an administrative penalty may not be less than $1,000 per violation per day. Each day that a violation remains uncorrected may be counted as a separate violation.

F.	Assessment of Administrative Penalties – By Violation Type

1.	The penalty assessed for public water systems serving more than 10,000 people will be determined by the type of violation. A violation is deemed type 1, type 2, or type 3. In no case will the penalty assessed pursuant to this subsection be less than $1,000 per violation per day.

- A type 1 violation is one that has a direct impact on public health, or that creates a serious risk to public health and/or an immediate threat to public health. The maximum penalty for a type 1 violation is $2,000 per violation per day.

A type 2 violation is one that may have a direct impact on public health but primarily involves non-compliance with technical safeguards. The maximum penalty is $1,500 per violation per day.

Type 3 violations are those that may have an indirect impact on public health and are generally related to poor record keeping. The penalty is $1,000 per violation per day.

2.	The penalty assessed for public water systems serving less than 10,000 people is determined by the type of violation (Type 1, 2 or 3) and type of public water system (PWS). The amounts set forth below will be assessed for each period of consecutive days during which a violation remains uncorrected.  If within two years of being assessed an administrative penalty for a violation, the PWS commits the same violation, the Department may assess a penalty in any amount permitted by statute notwithstanding the maximums set forth below.

a.	A type 1 violation is one that has a direct impact on public health, or that creates a serious risk to public health and/or an immediate threat to public health.

i.	Transient PWS: $750 per day, not to exceed $2,000;

ii.	Non-transient non-community PWS: $750 per day, not to exceed $3,000; and

iii.	Community PWS: $750 per day, not to exceed $4,000.

b.	Type 2 violations are those that may have a direct impact on public health but primarily involve non-compliance with technical safeguards. Such violations include but are not limited to failure to comply with monitoring requirements; and/or failure to complete public notification.

i.	Transient PWS: $750 per day, not to exceed $1,500;

ii.	Non-transient, non-community PWS: $750 per day, not to exceed $2,000; and

iii.	Community PWS: $750 per day, not to exceed $3,000

c.	Type 3 violations are those that may have an indirect impact on public health and are generally related to poor record keeping. Such violations include but are not limited to failure to submit monitoring or other required reports; late submittal of monitoring or other required reports; and/or failure to keep records on file as required.

i.	Transient PWS: $500;

ii.	Non-transient, non-community PWS: $750; and

iii.	Community PWS: $1,000

3.	The Department may impose a penalty in an amount that is less than the maximum listed in Section 2-B(F)(2) based on consideration of the following factors:

a.	Whether steps were taken by the public water system to prevent the violation;

b.	Whether steps were taken by the public water system to remediate or mitigate damages resulting from the violation;

c.	The financial condition of the public water system; and

d.	The best interest of the public.

4.	However, for public water systems serving more than 10,000 people, the penalty must not be reduced to less than $1,000 per day per violation.

## G.	Assessment of Administrative Penalties – Hearing

1.	Any person, against whom the Department assesses an administrative penalty for a violation of this rule or an administrative order, has the right to appeal by requesting an administrative hearing. The request for a hearing must be filed with the Department within 30 days after the service of notice of penalty assessment.

2.	The Hearing Officer's decision is deemed to be the Department's final agency action and is binding on the Department. If a public water system owner is aggrieved by this final decision, the right to judicial review is provided under Rule 80C of the Rule of Civil Procedure.

## H.	Assessment of Administrative Penalties – Enforcement

1.	The Department's assessment of an administrative penalty is a binding order on the person owning the public water system upon the person's election to waive, or failure to timely request, an administrative hearing. Each day for which the person fails to pay said penalty or otherwise fails to comply with an order of the Department, constitutes a separate and distinct violation, provided no administrative hearing is requested in a timely manner.

## I.	Administrative Penalty Schedule

1.	Type 1 Violations

a.	Failure to complete an engineering study/engineering order as required by 22 MRS §2612(4) and Section 2(D)(1) of this rule.

b.	Violation of an emergency order/boil order/do not drink order/ do not use order, as required by 22 MRS §2614 and Section 2(E) of this rule.

c.	Failure to apply appropriate disinfection to water treatment plants in accordance with Section 3(F)(2)(c) of this rule.

d.	Failure to apply appropriate disinfection of wells prior to the use of the wells as a source of public drinking water as required by Section 3(F)(2)(d) of this rule.

e.	Failure to appropriately disinfect a surface water source as required by Sections 3(H)(1)(a) and 7(H) of this rule.

f.	For systems using ground water sources, failure to install facilities for chlorinating as required by Section 3(H)(2)(a) of this rule.

g.	For systems using ground water sources, failure to store or use hazardous chemicals outside of the proximity of the well, as required at Section 3(H)(2)(b) of this rule.

h.	Failure to immediately report to the Department the occurrence of spills of hazardous chemicals within the wellhead protection area, as required by Sections 3(H)(2)(d) and Section 3(I)(2) of this rule.

i.	Failure to continuously disinfect a dug well or spring, if required by the Department pursuant to Section 4(D) of this rule.

j.	Failure of a community water system to provide a minimum positive pressure of 20 p.s.i. at the curb stop (curb cock), as required by Section 4(A) of this rule.

k.	Failure to comply with the maximum contaminant level requirements for inorganic chemicals, as required by Section 7(B) of this rule.

l.	Failure to comply with the maximum contaminant level requirements for organic chemicals, as required by Section 7(B) of this rule.

m.	Failure to comply with the maximum contaminant level requirements for radionuclides, as required by Section 7(B) of this rule.

n.	Failure to comply with the maximum contaminant level for inorganic contaminants, as required by Section 7(G)(3) of this rule.

o.	Failure to comply with the maximum contaminant level for inorganic contaminants, as required by Section 7(G)(3) of this rule.

p.	Failure to comply with the maximum contaminant level for microbiological contaminants, as required by Section 7(G)(4) and 7(Y) of this rule. .

q.	Failure to perform/complete a level assessment and/or corrective actions as required by Section (7)(Y) of this rule.	Failure to meet criteria for avoiding filtration, as required by Section 7(H) of this rule.

s.	Failure to meet disinfection requirements, as required by Section 7(H) of this rule.

t.	Failure to meet filtration requirements, as required by Section 7(H) of this rule.

u.	Failure to meet source water treatment requirements, as required by Section 7(I) of this rule.

v.	Failure to meet treatment technique requirements for lead and copper, as required by Section 7(K) of this rule.

w.	Failure to meet MCL and maximum residual disinfection level (hereafter MRDL) requirements, as required by Section 7(L) of this rule.

x.	Failure to follow specifications for the disinfection of water mains, as required by Section 3(F)(2)(a) of this rule.

y.	Failure to follow specifications for the disinfection of a water storage facility prior to being placed in service as required by Section 3(F)(2)(b) of this rule.

z.	Failure of a transient non-community water system that is in operation seasonally to complete required water tests for coliform bacteria and nitrate during the first 30 days of operation, as required by Section 3(G)(1) and (2) of this rule.

aa.	Failure of a new transient water system to complete appropriate tests prior to utilizing the source as a water supply, as required by Section 3(G)(2) of this rule.

bb.	Failure to maintain appropriate disinfectant residual or application rate, as required by Section 4(D) of this rule.

cc.	Failure to meet MRDL requirements for disinfection byproducts, as required by Section 7(G)(6) of this rule.

dd.	Failure to meet MCL requirements for residual disinfectant, as required by Section 7(G)(7) of this rule.

ee.	Failure to meet treatment technique requirements for disinfection byproducts, as required by 10-144 CMR 231 Section 7(L).

2.	Type 2 Violations

a.	Failure to employ a licensed water operator as required by 22 MRS §§ 2623, 2625, and 2630 and Section 2(B) of this rule.

b.	Failure to submit plans to be reviewed and approved by the Department specified by Section 3(C) of this rule.

c.	Failure to submit for approval plans to protect the surface supply watersheds as required by Section 3(G)(1)(a) of this rule.

d.	Failure to submit a map for approval that shows the watershed area delineation and potential sources of contamination, as required by Section 3(G)(1)(b) of this rule.

e.	Failure to submit the necessary well approval forms provided by the Department as part of the application process, as required by Section 3(G)(2) of this rule.

f.	Failure to discharge water softeners or other treatment techniques in an approved manner, as required by Section 3(H)(2)(e) of this rule.

g.	Failure of a community water system to have a sanitary seal at the termination of the well casing, as required by 3(H)(2)(f) of this rule.

h.	Failure to appropriately cover, disinfect and screen vents of reservoirs, as required by Section 4(B) of this rule.

i.	Failure to obtain a permit for a cross connection, as required by Section 4(F) of this rule.

j.	Failure to appropriately add fluoride, as required by Section 4(J) of this rule.

k.	Failure to comply with rules for bottling water for consumption, as required by Section 4(K) of this rule.

l.	Failure to monitor for coliform, as required by Section 7(C)(1)(a) of this rule.

m.	Failure to monitor for turbidity, as required by Section 7(C)(1)(b) of this rule.

n.	Failure to monitor for inorganic chemicals, as required by Section 7(C)(1)(c) of this rule.

o.	Failure to monitor for organic chemicals, as required by Section 7(C)(1)(d) of this rule.

p.	Failure to monitor for radionuclides, as required by Section (7)(C)(1)(e) of this rule.

q.	Failure to complete special monitoring for inorganic and organic chemicals, as required by Section 7(E)(1) of this rule.

r.	Failure to complete special monitoring for sodium, as required by Section 7(E)(2) of this rule.

s.	Failure to complete special monitoring for corrosivity characteristics, as required by Section 7(E)(3) of this rule.

t.	Failure to meet analytical and monitoring requirements for filtration and disinfection, as required by Section 7(H) of this rule.

u.	Failure to meet the monitoring requirements for lead and copper in tap water, as required by Section 7(I) of this rule.

v.	Failure to meet the monitoring requirements for water quality parameters, as required by Section 7(I) of this rule.

w.	Failure to meet monitoring requirements for lead and copper in source water, as required by Section 7(I) of this rule.

x.	Failure to comply with the requirements regarding non-centralized treatment devices, as required by Section 7(J) of this rule.

y.	Failure to comply with the siting requirements, as required by Section 7(A)(5) of this rule.

z.	Failure to comply with MCL requirements for turbidity, as required by Section 7(B) of this rule.

aa.	Failure to meet lead service line replacement requirements, as required by Section 7(I) of this rule.

bb.	Failure to meet public education and supplemental monitoring requirements, as required by Section 7(I) of this rule.

cc.	Failure to install and maintain appropriate hydrants, as required by Section 4(G) of this rule.

dd.	Failure to install appropriate curb stops (curb cocks), as required by Section 4(H) of this rule.

ee.	Failure to monitor for disinfectant residuals, as required by Section 7(L) of this rule.

ff.	Failure to comply with the compliance requirements regarding disinfection byproducts, as required by Section 7(L) of this rule.

gg.	Failure to meet filtration sampling requirements, as required by Section 7(P) of this rule.

hh. 	Failure to submit disinfection profiling and benchmarking, as required by Section 7(P) of this rule.

ii.	Failure to comply with the recycle provisions, as required by Section (7)(H) of this rule.

jj. 	Failure to provide appropriate public notification, as required by Section 7(Q) of this rule.

kk.	Failure to demonstrate completion of a State-approved start up procedure prior to serving water to the public each year as required by Section 7(Y) of this rule.

3.	Type 3 Violations

a.	Failure of a system to keep water analyses results, as required by this rule Section 5(A) of this rule.

b.	Failure of a system to keep records of actions taken by the system to correct violations of drinking water regulations, as required by Section 5(B) of this rule.

c.	Failure of a system to keep records of sanitary surveys, as required by Section 5(C) of this rule.

d.	Failure of a system to keep records regarding a variance or exemption, as required by Section 5(D) of this rule.

e.	Failure of a system to maintain daily operational records, as required by Section 5(E) of this rule.

f.	Failure to comply with any reporting requirements, as required by Section 6(A) of this rule.

g.	Failure to report analytical testing requirements by the tenth day of the following month in which the samples were analyzed, as required by Section 6(B) of this rule.

h.	Failure of a community water system serving municipalities or districts or any public water system that adds chemicals on a continuous basis to file with the Department no later than the tenth day of each month, monthly operational reports, as required by Section 6(C) of this rule.

i.	Failure to report test results as required by 1Section 7(D)(1) of this rule.

j.	Failure to provide appropriate public notification as required by Section 7(Q) of this rule.

k.	Failure to appropriately maintain records as required by Section 7(D) of this rule.

l.	Failure to provide appropriate public notice pertaining to lead as required by Section 7(I ) of this rule.

m.	Failure to report or provide public notification for certain unregulated contaminants, as required by Section 7(E) of this rule.

n.	Failure to meet reporting or record keeping requirements, as required by Section 7(H) of this rule.

o.	Failure to meet reporting requirements for lead and copper, as required by Section 7(I) of this rule.

p.	Failure to meet record keeping requirements for lead and copper, as required by Section 7(I) of this rule.

q.	Failure to meet the reporting requirements, as required by Section 7(O) of this rule.

r.	Failure to submit payment to the Department of the annual drinking water fee, as required by Section 2-A of this rule.

s.	Failure to have sanitary surveys conducted as part of the watershed, as required by Section 3(H)(1)(C) of this rule.

- Failure to meet reporting and recordkeeping requirements for disinfection byproducts, as required by Section 7(L) of this rule.

u.	Failure to meet reporting and record keeping requirements for turbidity, as required by Section 7(P) of this rule.

# SECTION 3: FACILITIES APPROVAL

Before initial construction of a new public water system, or before modification of any existing public water system in a manner which may affect the quality of water produced via treatment or other means, the public water system supplier or representative, pursuant to 22 MRS §2612, must first receive approval from the Department as set forth below.

## A.	Review Period

1.	All plans must be completed and submitted to the Department in a timely manner to allow the Department 30 days to review.

2.	Such submission must occur at least 30 days prior to the bid opening and at least 45 days prior to the start of construction of the project.

## B.	Siting Requirements Plans must demonstrate that the new public water system will meet the siting requirements set forth in Section 7(A)(5) of this rule.

## C.	Plan Submission

1.	Submission of Engineering Plans to the Department

a.	No new construction, addition, or alteration involving the source, treatment, or storage of water in any public water system may begin, until the public water system supplier or representative submits plans and specifications to the Department, and the Department has approved such new construction, addition or alteration in writing, unless such construction, addition, or alteration is exempted by Section 3(C)(3)(a)(i) or (ii)  of this rule. In granting approval of plans and specifications, the Department may require modifications, conditions, or procedures to ensure, as far as feasible, the protection of public health.

b.	Unless accompanied by plans and specifications bearing the seal of a Professional Engineer licensed in the State of Maine, the public water system must submit documentation of the costs for the proposed facility or water treatment system, or the cost of the modification or alteration of any existing system to the Department. The documentation must include the costs of all work, including labor and materials, to existing waterworks and any other information requested by the Department.

- The water system must make available for public review all information provided to the Department pursuant to Section 3(C)(3) if requested. This information must be presented at a location and in a manner that is convenient to the public water system’s customers.

2.	Preparation of Engineering Plans.  Plans and specifications for Public Water Systems must be prepared by a qualified professional and must bear the seal of a professional engineer as required by 32 MRS, Chapter 19, except for the following exemptions from plan submittal:

- Non-municipal projects with a total cost of less than $10,000.

- Municipal projects with a total cost of less than $250,000

3.	Exemptions

a.	The following activities are exempt from the requirement for approval by the Department:

i.	Maintenance activities for existing facilities, which do not involve the storage or treatment of finished water (filtered, treated, etc.).

ii.	Replacement of water mains or installation of new water mains provided they are disinfected and pressure tested in accordance with the AWWA standards indicated in Section 3(F) of this rule.

b.	Examples of activities that are not exempted in this section and require approval by the Department first include but are not limited to, the painting and/or repair of standpipes, reservoirs, or any storage facility that has contact with finished water.

## D.	General Operations Permit

1.	Any new community or non-transient, non-community public water system commencing operation , must first obtain a general operations permit from the Department.

a.	To obtain a general operations permit for a new community or non-transient, non-community public water system, the owner, or the owner’s designee, must submit sufficient plans, specifications, and documentation demonstrating adequate technical, financial and managerial capacity.

b.	Applications for general operations permits must be made on forms provided by the Department. These forms must be submitted and approved by the Department before the public water system begins operations.

## E.	Demonstration of Capacity

In order to obtain a general operations permit from the Department, a public water system must demonstrate technical, managerial, and financial capacity.

1.	Technical capacity may be demonstrated by a number of methods, including, but not limited to, the following:

- Engineering plans or schematics and drawings of treatment facilities;

- Adequate drawings, diagrams, schematics and maps of the distribution system or plumbing components;

- An adequate number of State-licensed operators of the requisite classification;

- Source water protection plans and maps of the watershed or wellhead protection area; and

- Any other relevant documentation requested by the Department.

2.	Financial capacity may be demonstrated by a number of methods, including, but not limited to, the following:

a.	Annual and projected budgets;

b.	Identification of individual(s) responsible for water system operations, including procedures related to financial decisions affecting the water system;

c.	Copies of rate case determination documents for water systems regulated by the Public Utilities Commission; and

e.	Any other relevant financial information requested by the Department.

3.	Managerial capacity may be demonstrated by a number of methods, including, but not limited to, the following:

a.	Demonstrated knowledge of the number of water system service connections and the population served;

b.	Clear, definitive identification of the water system owner(s);

c.	Identification of the primary contact person(s) responsible for communicating with the Department;

d.	Identification of personnel responsible for daily operations of the water system;

e.	Plans for continuing education, training or professional development or staff;

f.	Formalized routine operations and maintenance procedures in the form of written standard operating procedures and policies;

g.	Description of record keeping procedures employed;

h.	Written emergency procedures and/or an emergency response plan, including identification of persons or organizations contacted in the event of an emergency; and

i.	Any other relevant information requested by the Department.

## F.	Construction Standards

1.	Applicable standards such as those established by the American Water Works Association’s (AWWA) Recommended Standards for Water Works and NSF / ANSI Standards for Drinking Water Treatment Units must be consulted as well as engineering standards published by other generally accepted organizations.

2.	Disinfection

a.	The AWWA C-651-14 specification for the disinfection of water mains must be utilized for all water main construction except that the tablet method must not be used unless specifically approved in writing by the Department.

b.	AWWA C-652-11 specification for the disinfection of water storage facilities must be utilized prior to having any storage facility go into service, whether it is a new tank, or an existing tank that has undergone interior maintenance.

c.	AWWA C-653-13 specification for disinfection of water treatment plants must be utilized prior to providing water for consumption.

d.	AWWA C-654-13 for the disinfection of wells must be utilized prior to the use of those wells as a source of public drinking water.

3.	All water mains and services being used for the purposes of transporting potable water must be pressure tested in accordance with AWWA Standard for pressure testing.

4.	Well Construction

a. 	All newly constructed wells and wells modified by additional drilling casing alterations or hydrofracturing must be constructed or altered in compliance with the Maine Well Drillers and Pump Installers Rules (10-144 CMR, Chapter 232) and one of the following standards:

i.	AWWA’s Standard A100-15, Recommended Standards for Water Works, 2012 Edition, herein incorporated by reference; or

      - The National Ground Water Association’s Manual of Water Well Construction Practices (3rd Edition), herein incorporated by reference.

In the event that one of the above standards conflicts with State or federal rules, the State or federal rules will take precedent.

b.	Newly constructed wells serving community, transient non-community and non-transient, non-community water systems must be constructed as described in the preliminary approval process, which is included in the Department’s application packet and described in Section 3(G)(2) of this rule. The Department may require wells with reduced setbacks from septic system components or other potential sources of contamination to include additional steel casing or a PVC liner and top and bottom well seals, as described in Maine’s Well Drillers and Pump Installers Rules (10-144 CMR Ch. 232, Chapter 4).

c.	Wells determined by the Department to pose significant risk from sources of contamination are required to be grouted using methods and materials described in Maine’s Well Drillers and Pump Installers Rules (10-144 CMR 232, Section 400.7.3).

5.	Abandonment of Wells

The Department may require a public water system to abandon a well if the Department determines that the well constitutes a significant threat to public health. Abandonment must meet the requirements of Maine’s Well Drillers and Pump Installers Rules (10-144 CMR Chapter 232).

6.	NSF/ANSI Standard 60

a.	All chemicals added to drinking water must be certified to meet NSF/ANSI Standard 60 - 2017: Drinking Water Treatment Chemicals – Health Effects. Certification must be performed by an ANSI-accredited, third-party testing and certification organization.

b.	The Department reserves the authority to waive this Standard 60 certification requirement on a case-by-case basis, in accordance with applicable law.

c.	Evidence for this requirement is met, if the chemical shipping container labels or Safety data sheets include:

i. 	Chemical name, purity and concentrations, supplier name and address; and

ii.	Labeling indicating compliance with NSF/ANSI Standard 60.

d.	Compliance with these standards must be met at the point of delivery.

7.	NSF/ANSI/CAN Standard 61

a.	All materials, products and coatings that contact drinking water installed or applied must be certified to meet NSF/ANSI/CAN Standard 61-2022: Drinking Water System Components – Health Effects. Certification must be granted by an ANSI-Accredited, third-party testing and certification organization.

b.	Exemptions may include the following:

i.	Miscellaneous valves and fittings, three-inch diameter and smaller, may be exempt from this requirement if NSF/ANSI/CAN 61 Certified products are not readily available;

ii.	Steel well casing;

iii.	Existing stocks of materials. When stocks need to be reordered, the new materials must comply with this section;

iv.	A concrete structure, tank, or treatment tank basin constructed onsite that is not normally coated or sealed. If a coating or sealant is specified by the design engineer, the coating or sealant must be certified to comply with ANSI/NSF/CAN Standard 61;

v.	An earthen reservoir or canal located upstream of water treatment;

vi.	A synthetic tank constructed of material that meets Food and Drug Administration standards for a material that comes into contact with drinking water or aqueous food, or a galvanized steel tank, either of which is:

1)	Less than 15,000 gallons in capacity; and

2)	Used in a public water system with 500 or fewer service connections;

vii.	A pipe, treatment plant component, or water distribution system component made of lead-free stainless steel; and

viii.	Any other conditions deemed appropriate by the Department, in accordance with applicable law.

8.	All new community public water systems must install a flow meter that will provide continuous, cumulative measurement of the water system flow, and maintain records of flow.

9.	All public water systems must have a sampling port prior to any treatment and/or storage, including pressure tanks, which enables the collection of water directly from each water source (raw water sampling port).

## G.	New Sources

1.	New Surface Water Sources

- Plans for the protection of surface supply watersheds must be submitted to the Department prior to the Department’s approval of any surface water source. These plans must include the following:

i.	A description of public education procedures and materials the system plans to implement or distribute to inform its consumers and all parties that come in contact with the watershed or water source of watershed issues that affect the water quality of the surface water source;

ii.	Demonstration of sufficient control over the watershed, evidenced by one of the following:

- Ownership of the property;

- A contractual agreement with the owners of the property that ensures that the surface water source is not to be negatively impacted by the watershed; or

- A plan presented to the Department for approval showing how the watershed will be sufficiently protected. The plan must be submitted to the Department in writing and be prepared by an appropriate individual qualified to prepare such a plan; and

iii.	A description of other appropriate protection measures to ensure that the surface water source will maintain high quality water.

b.	Maps showing the watershed area delineation and potential sources of contamination and their types and land ownership must be submitted to the Department with the request for source approval. Potential sources of contamination include, but are not limited to, sanitary landfills, dumps, oil storage facilities, chemical storage facilities, septage disposal areas, spray irrigation areas, farming operations which utilize large amounts of pesticides, all enterprises which require hazardous waste permits, major industries, and highways commonly used in the transport of hazardous materials.

c.	Analysis

i.	Final approval of the finished surface water source may be granted by the Department only after all required water quality analyses are completed and the Department further determines that the source is in compliance with all applicable National Primary Drinking Water Regulations (40 CFR Parts 140-143).

ii.	Transient water systems. For transient, non-community water systems, untreated water samples must be analyzed by a certified laboratory, prior to source approval, for the parameters in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants; and

- Inorganic contaminants.

iii.	Non-transient non-community water systems. For non-transient non-community systems, untreated water samples must be analyzed by a certified laboratory, prior to source approval, for the parameters listed in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants; and

- Radionuclide contaminants.

iv.	Community water systems. For community water systems, untreated water samples must be analyzed by a certified laboratory, prior to source approval, for the parameters listed in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants; and

- Radionuclide contaminants.

v.	Bottled water systems. For bottled water systems, untreated water samples must be analyzed by a certified laboratory, prior to source approval, for the parameters listed in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants; and

- Radionuclide contaminants

vi.	Water quality measurements for turbidity, free chlorine residual, temperature, alkalinity and pH may be performed by any person acceptable to the Department. The ability of individuals to properly conduct tests for these parameters will be evaluated by the Department during sanitary surveys.

d.	Treatment required (See Section 7(H) and 40 CFR Subpart H 141.70-141.76, Subpart T and Subpart W, regarding filtration and disinfection requirements) that are mandatory for all surface water systems.

e.	All new community surface water systems must evaluate their system design capacity and submit a report to the Department using forms provided by the Department. The Department will determine system design capacity for each surface water source as part of a new system and source approval.

f.	The Department will approve an intake located within two miles of a public boat launch only if the public water system submits a risk assessment that is satisfactory to the Department.

2.	New Ground Water Sources

a.	Transient non-community water systems and non-transient non-community water systems

i.	Transient non-community water systems and non-transient non-community water systems must complete and submit the required Department forms at least 30 days prior to the proposed date of drilling/installation/activation. Required documentation includes the Department’s Request for Preliminary Approval Form, a location map and a site plan showing all potential sources of contamination within 300 feet of the proposed well location. Other documentation may be requested on a case-by-case basis if the Department determines that such information is necessary to better understand the proposed well location, conditions, or, otherwise, for the protection of public health.

ii.	The Department will review the documents required by Section 3(G)(2)(a)(i) above, to determine whether the well location adequately provides safe and healthy drinking water to the public. No production well may be installed until the Department grants preliminary approval in writing to the public water system supplier or representative.

iii.	New wells must be located at least 300 feet away from potential contamination sources and at least 1,000 feet away from underground storage tanks regulated by the Department of Environmental Protection (DEP), in accordance with Maine Rules for Underground Oil Storage Facilities (06-696 CMR Chapter 691, Amended April 3, 2016), unless a waiver is obtained from the Department and the DEP.

iv.	The Department may grant a setback waiver on a case-by-case basis for wells that must be placed closer than 300 feet from a potential contamination source. The Department must receive information from an appropriately qualified professional hired by the public water system. For any well proposed less than 150 feet from one or more subsurface disposal fields, a Maine certified geologist’s hydrogeologic assessment must be presented to the Department for review and approval. The assessment must include a description of the local surficial geology, a pre-pumping water table contour map, a map showing the water table contours under pumping conditions and an evaluation of the site’s physical characteristics which mitigate any potential impacts to the well from the disposal field(s). Alternatively, the water system must submit plans for an advanced treatment unit (ATU) designed to pre-treat all septic system effluent prior to discharge to the septic system disposal field, to be reviewed and evaluated by the Department. Any pretreatment system proposed as mitigation for reduced setbacks from septic system components must be shown to significantly reduce nitrate, nitrite, and bacteria levels and include a plan for ongoing maintenance. The Department may waive these requirements on a case-by-case review or require additional information to ensure that the proposed well location is not safe from threats of contamination or potential threats of contamination even with increased monitoring for those contaminants.

v.	The methods and standards described in the Manual for Water Well Construction Practices, 3rd Edition, (published in 1998 by the National Ground Water Association), must be used for the proper development and determination of safe yield for all proposed transient non-community and non-transient non-community wells. Well drillers may consult with the Department to determine a safe yield if the manual does not  provide sufficient information. A copy of this Manual is available by calling the Department’s office at (207) 287-2070.

vi.	 All water quality samples must be collected after proper well development, disinfection, and the conclusion of continuous pumping on the well for a sufficient period of time so that a minimum of three well bore volumes have been removed.

vii.	Department may, on a case-by-case basis, require a report be prepared by an appropriately qualified person or firm evaluating the well which may include: a description of the site geology and any sources of contamination in the area; a map of the area showing all wells installed and any potential sources of contamination in the area; drilling logs for each well installed; pump test drawdown data if available; recommendations for wellhead protection area delineations; and all required water quality analysis results. The report must be submitted to the Department for review with the request for final approval.

viii.	The Department will only grant final approval of the proposed well after the public water system reports all required water quality analyses and the Department determines that the well is in compliance with all applicable drinking water standards and regulations or has received an appropriate variance.

ix.	The public water system must complete and submit the required Department forms and reports with all water quality analyses results and any maps to the Department for review and approval. Wellhead protection area delineations must be made using one or more methodologies approved by the Department.

x.	The public water system may not use the proposed new source until the Department grants final written approval of the proposed well. The Department may grant conditional approval in cases where some requirements have not been completed, but the Department has determined that the pending information or changes are not a significant risk to public health. Such cases may include, but are not limited to, a laboratory delay in analyzing and reporting non-acute water test. The Department may also require additional treatment, testing or other requirements that the Department deems necessary for the protection of public health.

xi.	Analysis

a)	Transient water systems

1)	The Department will only grant final approval of any proposed well after all required water quality analyses are completed and the Department further determines that the well complies with all applicable National Primary Drinking Water Regulations (40 CFR Parts 141-143).

2)	Untreated water samples must be analyzed by a certified laboratory, prior to source approval and after proper well development and safe-yield determination, for the parameters in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants. If total coliform results are positive, then samples must be analyzed for E. coli. If the Department determines that the proposed well potentially contains groundwater under the influence of surface water, then samples must be analyzed for both total coliform bacteria, as well as heterotrophic plate count (HPC)-per approved methods authorized in 40 CFR § 141.74;

- Inorganic contaminants; and

- Volatile organic contaminants (if source is within 1,000 feet of an underground storage tank).

3)	The Department may require additional testing, if a contamination event has occurred in the area.

b)	Non-community non-transient water systems

1)	The Department will only grant final approval of any proposed well after all required water quality analyses are completed and the Department further determines that the well complies with all applicable National Primary Drinking Water Regulations (40 CFR Parts 141-143).

2)	Untreated water samples must be analyzed by a certified laboratory, prior to source approval and after proper well development and safe-yield determination, for the parameters in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants If total coliform results are positive, then samples must be analyzed for E. coli. If the Department determines that the proposed well potentially contains groundwater under the influence of surface water, then samples must be analyzed for both total coliform bacteria, as well as heterotrophic plate count-HPC-per approved methods authorized in 40 CFR § 141.74;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants;

- Per- and Polyfluoroalkyl Substances (PFAS) (Per approved methods authorized in the July 1, 2024 edition of the National Primary Drinking Water Regulations at 40 CFR § 141.24), including all PFAS compounds included in the standard list of analytes for the method; and

- Radionuclide contaminants

- Combined radium (radium 226 and 228) if gross alpha is ≥ 5 pCi/L.

3)	The Department may modify the list of required water quality test parameters prior to approval if the determination is made that the testing required will ensure that the well can produce safe and potable water or otherwise for the protection of the public health.

b.	Community public water systems serving fewer than 250 people

i.	Community public water systems serving fewer than 250 people must complete and submit the required Department forms for each proposed well, at least 30 days prior to the proposed date of drilling/installation/activation. Required documentation includes a location map, estimated quantity of water required from the well in gallons per minute or gallons per day, and a site plan showing all potential sources of contamination within 1,000 feet of the proposed well. The Department may require a preliminary hydrogeologic investigation of a well location if additional information is necessary to evaluate the adequacy of the site to provide a safe supply of water to the public or otherwise to protect the public health.

ii.	The Department will review the documents required by Section 3(G)(2)(d)(i) to determine whether the well location provides safe and healthy drinking water to the public. The Department will grant any preliminary approval in writing, which is required before a public water system may install a production well.

iii.	New wells must be located at least 300 feet away from potential contamination sources and at least 1,000 feet from underground storage tanks (in accordance with DEP’s Rules for Underground Oil Storage Facilities (06-096 CMR Chapter 691, amended April 3, 2016)) unless a waiver is obtained from the Department grants a waiver for this setback.

iv.	If a proposed well must be placed closer than 300 feet from a potential contamination source, the Department may grant a setback waiver based on an evaluation of geologic conditions, individual land use, and other factors that potentially affect water quality. The Department must receive information from an appropriately-qualified professional hired by the public water system. system. Any proposal for a well located less than 150 feet from one or more subsurface disposal fields must include a Maine certified geologist’s hydrogeologic assessment for the Department’s review and approval. The assessment must include a description of the local surficial geology, a pre-pumping water table contour map, a map showing the water table contours under pumping conditions and an evaluation of the physical characteristics of the site which mitigate any potential impacts to the well from the disposal field(s). Alternatively, the public water system must submit plans for an advanced treatment unit (ATU) designed to pre-treat all septic system effluent prior to discharge to the septic system disposal field, to be reviewed and evaluated by the Department. Any pretreatment system proposed as mitigation for reduced setbacks from septic system components must be shown to significantly reduce nitrate, nitrite and bacteria levels and include a plan for ongoing maintenance. The Department may waive these requirements when it determines that the information is not required. The Department may require additional information to ensure the suitability of the proposed well for use as a public water supply system. The Department may place conditions on a waiver granted, which may include increased water quality monitoring for specific contaminants at a schedule and frequency to be determined by the Department.

v.	Treatment for all new wells may be required as described in Section 3(G)(2)(j) of this rule.

vi.	The Department may deny a proposed well location if it determines that a proposed well location is not safe from threats of contamination or potential threats of contamination even with increased monitoring for those contaminants.

vii.	The methods and standards described in the Manual for Water Well Construction Practices, 3rd Edition, (published in 1998 by the National Ground Water Association), must be used in proper development and determination of safe yield for all proposed community wells serving fewer than 250 people. A copy of the Manual is available by calling the Department at (207) 287-2070. The process for determining safe yield must be approved by the Department prior to drilling the well. All water quality samples must be collected after proper well development, disinfection, and at the conclusion of continuous pumping on the well for a sufficient period time so that a minimum of three well bore volumes have been removed. The Department may, on a case-by-case basis, require a report to be prepared by a certified geologist or professional engineer evaluating the well, based on an evaluation of geologic conditions, individual land use, and other factors that potentially affect water quality. This report may be required to include: a description of the site geology and any sources of contamination in the area; a map of the area showing all wells installed and any potential sources of contamination in the protection areas; drilling logs for each well installed; pump test drawdown data if available; recommendations for wellhead protection area delineations; and all required water quality analysis results. The report must be submitted to the Department for review with the request for final approval.

viii.	For all production wells for community water systems serving fewer than 250 people the owner, operator or other duly responsible representative of the public water supply must acquire sufficient land use control of all land within the minimum wellhead protection areas specified in the pump test report prior to final approval. Sufficient land use control means:

a)	Ownership of the property;

b)	A contractual agreement or easement with the owners of the property that ensures that the well must not be negatively impacted by activities in the contributing area; or

c)	A plan presented to the Department for review and approval showing how the contributing area will be sufficiently protected. The plan must be submitted to the Department in writing and be prepared by an appropriately qualified individual.

In addition, the public water system must provide to the Department a description of public education procedures and materials the public water system plans to implement or distribute to inform its consumers and owners of property within the identified protection areas of water quality and wellhead protection issues. The Department may provide technical assistance to public water systems drafting these educational strategies.

ix.	Final approval of the proposed well may be granted only after all required water quality analyses have been completed and it is further determined that the well is in compliance with all applicable National Primary Drinking Water Regulations (40 CFR Parts 141-143).

x.	The public water supplier or representative must complete and submit all required Department forms, along with all water quality analysis results, evidence of land use controls, and all required maps and reports to the Department for review and approval.

xi.	The public water system may not use the proposed new source until the Department has granted final approval in writing. The Department may grant conditional approval on a case-by-case basis, if no potential contamination is identified. The Department may also require additional treatment, testing or other requirements that the Department deems necessary for the protection of the public health, based on an evaluation of geologic conditions, individual land use and other factors that potentially affect water quality.

xii.	Analysis

a)	Community public water systems serving fewer than 250 people

1)	Final approval of the proposed well may be granted by the Department only after all required water quality analyses are completed and it is further determined that the well is in compliance with all applicable National Primary Drinking Water Regulations at 40 CFR Parts 141-143.

2)	Untreated water samples must be collected and analyzed by a certified laboratory, prior to source approval, and after proper well development and determination of safe yield for the parameters in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminants If total coliform results are positive, then samples must be analyzed for E. coli. If the Department determines that there is potential groundwater under the influence of surface water, then samples must be analyzed for microscopic particulate analysis (MPA), per approved EPA method “Consensus Method for Determining Groundwaters Under the Direct Influence of Surface Water Using Microscopic Particulate Analysis (MPA)”;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants;

- Per- and Polyfluoroalkyl Substances (PFAS) (Per approved methods authorized in the July 1, 2024 edition of the National Primary Drinking Water Regulations at 40 CFR § 141.24), including all PFAS compounds included in the standard list of analytes for the method; and

- Radionuclide contaminants.

c.	Community public water systems serving 250 people or more

i.	Community public water systems serving 250 people or more must complete and submit the required Department forms along with any other Department-required documentation, at least 30 days prior to the proposed date of drilling/installation/activation. Required documentation includes but is not limited to, the Department’s Preliminary Approval Form, a location map, estimated quantity of water required from the well in gallons per minute, and a site plan showing all potential sources of contamination within 2,500 feet of the proposed well location. The Department may require a preliminary hydrogeologic investigation of a site if it determines that additional information is required to evaluate the adequacy of the well to provide a safe supply of water to the public or otherwise to protect the public health.

ii.	All required documents will be reviewed by the Department to determine the adequacy of the well location to provide safe and healthy drinking water to the public. No production well may be installed before the Department has granted preliminary approval.

iii.	New wells must be located at least 300 feet away from potential contamination sources and at least 1,000 feet from underground storage tanks regulated by DEP, in accordance with Maine Rules for Underground Oil Storage Facilities (06-096 CMR Chapter 691), unless a waiver is obtained from the Department and DEP, after both departments evaluate geologic conditions, individual land use and other factors potentially affecting water quality. If the Department determines that a setback distance greater than 300 feet is required to protect public health, then the public water system may be required to drill a well at a greater setback distance.

iv.	If a proposed well must be placed within 300 feet from a potential contamination source, then the Department may grant a setback waiver on a case-by-case basis, based on an evaluation of geologic conditions, individual land use and other factors potentially affecting water quality. The Department must receive information from an appropriately-qualified professional hired by the public water system. Any well proposed less than 150 feet from one or more subsurface disposal fields must include a Maine certified geologist’s hydrogeologic assessment that is presented to the Department for review and approval. Assessments include a description of the local surficial geology (and bedrock geology, if applicable), a pre-pumping water table contour map, a map showing the water table contours under pumping conditions and an evaluation of the physical characteristics of the site which mitigate any potential impacts to the well from the disposal field(s). Alternatively, the public water system must submit plans for an advanced treatment unit (ATU) designed to pre-treat all septic system effluent prior to discharge to the septic system disposal field, to be reviewed and evaluated by the Department.  Any pretreatment system proposed as mitigation for reduced setbacks from septic system components must be shown to significantly reduce nitrate, nitrite, and bacteria levels and include a plan for ongoing maintenance. The Department may waive these requirements on a case-by-case review or require additional information to ensure the suitability of the proposed well for use as a public water supply source. This waiver is only granted after an evaluation of geologic conditions, individual land use and other factors potentially affecting water quality. The Department may place conditions on a setback waiver which may include increased water quality monitoring for specific contaminants at a schedule and frequency to be determined by the Department.

v.	Treatment for all new wells may also be required as described in Section 3(G)(2)(j) of this rule.

vi.	The Department may deny a request for approval if it determines that the proposed well location is not safe from threats of contamination or potential threats of contamination even with increased monitoring for those contaminants.

vii.	For all proposed wells, a prolonged pump test will be required prior to final approval. The requirements of the pump test are described in subsequent parts of this section, 3(G)(2)(c)(viii) through (xix).

viii.	For all production wells for community water systems serving more than 250 people a plan showing all test well locations and a description of the pump test methodology must be submitted to the Department for approval at least two weeks prior to the running of the prolonged pump test. Drawdown readings must be recorded in the production well.

ix.	For all surficial wells the pump test must be run for at least 48 hours and continue until stabilization has been reached or for five days, whichever is less. Stabilization is considered to be reached when the drawdown reading at an observation well near the production well or the production well has not varied by more than one-half inch during the preceding 24-hour period. An alternative definition of stabilization may be proposed by the applicant and must be reviewed and approved by the Department prior to implementation. The proposal must be prepared by an appropriately qualified person or firm.

x.	For all surficial wells, a report describing and evaluating the pump test must be prepared by an appropriately qualified person or firm and must include: a description of the site geology and all potential sources of contamination in the area; a map showing the locations of all monitoring and production wells used for the pump test, the pre-pumping ground water contours, potential sources of contamination in the area; a map showing ground water contours under pumping conditions; and wellhead protection area delineations. Wellhead protection area delineations must be made using one or more methodologies approved by the Department.

xi.	For all surficial wells, the safe yield, area of influence, and minimum protective zone of the well must be presented in the pump test report.

xii.	For all bedrock wells, a prolonged pump test of not less than 48 hours must be performed terminating when the safe yield of the well can be reasonably estimated by an appropriately qualified person of firm.

xiii.	For all bedrock wells, a report describing and evaluating the pump test must be prepared by a Maine certified geologist or professional engineer and must include: a description of the site geology and all potential sources of contamination in the area; a map showing the locations of all monitoring and production wells; and recommendations for wellhead protection.

xiv.	For all production wells for community water systems serving more than 250 people, the owner, operator or other duly responsible representative of the public water system must acquire sufficient land use controls of all land within the minimum wellhead protection areas specified in the pump test report prior to the Department’s final approval. This land use control must be evidenced by documentation of such control, which must be provided to the Department. Sufficient land use control means:

a)	Ownership of the property;

b)	A contractual agreement or easement with the owners of the property that ensures that the well will not be negatively impacted by activities in the contributing area; or

c)	A plan showing how the contributing area will be sufficiently protected. The plan must be submitted to the Department in writing for review and approval and be prepared by an appropriately qualified individual.

xv.	In addition, the public water system must submit to the Department a description of public education procedures and materials planned for  informing its customers and owners of property within the identified protection areas of water quality and wellhead protection issues. The Department may provide technical assistance to public water systems drafting these educational strategies.

xvi.	Water quality samples must be collected at the conclusion of the prolonged pump test. Final approval of the proposed well may be granted only after all required water quality analyses have been completed and it is further determined that the well is in compliance with all applicable National Primary Drinking Water Regulations (40 CFR Parts 141-143).

xvii.	All Department-required approval forms (or equivalent) must be submitted along with all water quality analyses results, evidence of land use controls, as well as all required maps and reports, to the Department for review and approval.

xviii.	The public water system may not use the proposed new source until the Department has provided final approval in writing. The Department may grant conditional approval on a case-by-case basis, based on an evaluation of geologic conditions, individual land use and other factors potentially affecting water quality. The Department may also require additional treatment, testing or other requirements that the Department deems necessary for the protection of public health.

xix.	Analysis

a)	Community water systems serving more than 250 people.

1)	Untreated water samples must be analyzed by a certified laboratory, prior to source approval and after proper well development and safe-yield determination for the parameters in Appendix A. The CFR reference is listed in the tables for each of the required contaminants:

- Microbial contaminant If total coliform results are positive, then samples must be analyzed for E. coli. If the Department determines that there is potential groundwater under the influence of surface water, then samples must be analyzed for microscopic particulate analysis (MPA), per approved EPA method “Consensus Method for Determining Groundwaters Under the Direct Influence of Surface Water Using Microscopic Particulate Analysis (MPA)”;

- Inorganic contaminants;

- Volatile organic contaminants;

- Synthetic organic contaminants;

- Per- and Polyfluoroalkyl Substances (PFAS) (Per approved methods authorized in the July 1, 2024 edition of the National Primary Drinking Water Regulations at 40 CFR § 141.24), including all PFAS compounds included in the standard list of analytes for the method; and

- Radionuclide contaminants.

d.	Bottled Water Systems

i.	Bottled water systems will be required to conduct new well approval sampling on groundwater sources in the same manner as community water systems serving more than 250 people unless otherwise noted in Section 3(J), Bottled Water Approval.

e.	New dug wells and springs for all public water systems

i.	All proposed dug wells and springs must be considered surface water sources and meet the requirements of the surface water source approval section of this rule (Section 3(G)(1)).

f.	Well termination

i.	All public water system wells must terminate no less than 18 inches above the ground surface or be contained in a sealed, watertight pit, and have a sanitary seal well cap with a protected, screened vent at the termination of the well casing.

g.	Treatment required

i.	All community water systems that use ground water sources and serve municipalities and/or districts must have chlorination facilities.

ii.	All new community ground water supplies serving municipalities and/or districts may be required by the Department to continuously chlorinate for a period of 2 months following initial utilization. The Department may require further raw water testing following the 2-month period of chlorination.

iii.	Prior to source approval, treatment approved by the Department, must be installed for any contaminant (except for sodium) found to be in excess of the maximum contaminant level. Sodium is regulated by Section 7(E) of this rule.

iv.	The Department may, at its option, require the installation of treatment equipment if a contaminant is present in sufficient quantity to constitute a public health concern in the future, even if the contaminant level does not exceed the current maximum contaminant level. The Department, in such cases, must provide an opportunity for appeals, hearings and reviews.

v.	All public drinking water system sources determined to be ground water sources under the direct influence of surface waters must comply with the requirements listed in Section 7(H) regarding filtration and disinfection.

h.	Review period for plans submitted either for preliminary or final well approval

i.	The Department will review and make a decision on an application within 30 days of receiving a complete application. The review and approval period begins when the Department has received all information requested and the information provided is sufficient for the Department to make an informed decision.

## H.	Existing Sources

1.	Surface Water Systems

a.	All existing public surface water systems using surface water sources, including systems using ground water under the direct influence of surface water, must  filter and continuously disinfect the water with chlorine or by some other means approved by the Department unless the water system meets all criteria for avoiding filtration pursuant to  Section (7)(H) of this rule.

b.	If applicable, areas within 200 feet of intakes must be land-use restricted by means of deed, easement, or other legal document.

c.	Public water systems supplying unfiltered surface water and/or ground water under the direct influence of surface water must have a watershed inspection conducted at least annually and provide a report of each such inspection to the Department. The annual watershed inspection must evaluate water source protection, associated facilities and equipment and review operational procedures and maintenance records for the purpose of evaluating the adequacy of programs and procedures, such as source water protection, facilities and equipment operations and maintenance, etc., to produce and distribute safe drinking water. (See Section (7)(H), which incorporates by reference 40 CFR 141.70 through 141.75.

2.	Ground Water Systems

a.	Community water systems using ground water sources must provide facilities for chlorination.

b.	Hazardous chemicals (e.g. pesticides, petroleum products, degreasers, etc.) must not be used or stored in the proximity of the well, except when used in water treatment.

c.	Any hazardous chemical used in water treatment must be stored in such a manner that it will be completely contained and not enter the aquifer.

d.	The occurrence of spills of hazardous substances within the wellhead protection area shall be immediately reported to the Department by the water supplier upon knowledge of such an accident.

e.	All discharges from water softeners or other treatment techniques must be made in an approved manner.

f.	All public water system wells shall have a sanitary seal well cap with a protected, screened vent at the termination of the well casing.

g. 	All existing public water system wells which are modified, altered or repaired, including by hydrofracturing, in a manner that may change the yield or chemistry of the water served must comply with Section 3(F)(3) and be approved by the Department prior to commencement of the modifications, alterations, repairs or hydrofracturing. Based on an evaluation of geologic conditions, individual land use and other factors potentially affecting water quality, the Department may require additional testing to demonstrate safe water quality following such modifications. The Department may require water treatment to ensure compliance with this rule.

## I.	Protective Measures

1.	Public water system suppliers must follow an active program for watershed and wellhead protection. Emergency response plans must be designed by the respective suppliers.

2.	The occurrence of spills of hazardous substances within the watershed must be immediately reported to the Department by the public water system supplier or representative, upon knowledge of such an incident by calling (207) 287-2070 during normal office hours, or the 24-hour emergency number (207) 557-4214.

J.	Bottled Water Approval

1.	General Requirements: No person may extract or treat water for bottling in the State of Maine without first obtaining Department approval by demonstrating that the treatment and raw source water quality meet the requirements of this rule. Approval consists of an application review process, where the applicant must provide the following documentation to the Department:

a.	Application. A completed application;

b.	Report of water quality results. Any applicable test results that the Department deems necessary at time of application, due to surrounding environmental conditions or other circumstances that may indicate a threat of contamination to the well and potentially result in an adverse health impact on customers. Such monitoring must be performed at regular intervals, as determined by the Department, with testing/monitoring results reported to the Department within the established time frames;

c.	Report of raw water test results for all physical, chemical, microbiological and radiological parameters specified in Appendix A of this rule; and

d.	Hydrogeologic Report. A report on the regional geology surrounding the site and the specific site geology, including a description of the vertical and horizontal extent of the source aquifer using existing data. The information will be used to define the recharge area of the aquifer, or, in the case of regional aquifers, the zone of influence of the subject source. A report detailing the development of the source; the method of construction, including spring design, well installation, surface catchment, and intake structures; and transmission facilities as appropriate, is required. A watershed survey of the recharge area or zone of influence of subject source that identifies and evaluates actual and potential sources of contamination must be provided to the Department. A minimum 48-hour pump test must be conducted on each well, to determine safe yield. Based on the findings in the hydrogeologic report, a plan may be required for special monitoring of any significant contamination source and for taking restrictive preventative or corrective measures, as appropriate, to protect the source water. Such a report must be completed and submitted by a Maine-certified geologist. Water vending machines are exempt from this requirement to submit a hydrogeologic report.

2.	Comply with DEP requirements for significant groundwater withdrawals.

c.	“Significant Groundwater Well” does not apply to or include, the following:

i.	A public water system well, except for those public water systems solely bottling water for sale;

ii.	Individual home domestic supply;

iii.	Agricultural use or storage;

iv.	Development or part of a development requiring a permit, pursuant to Article 6, Article 7, or Article 8-A; or

v.	A structure or development requiring a permit from the Maine Land Use Planning Commission, in accordance with 12 MRS § 685-B.

3.	Approval of Bottled Water Sources

- Approval required. The source water (e.g. spring, bore hole, well, etc.) of all bottled or   water offered or exposed for sale or distribution within the State of Maine, or meeting the definition of a public water system, must receive prior approval from the Department.

b.	General source requirements. All sources must meet the Department’s water quality requirements in Appendix A of this rule. Final approval of the proposed sources may be granted by the Department only after all required water quality analyses have been completed and it is further determined that the well is in compliance with Appendix A of this rule.

4.	Approval of Bottled Water Facilities

a.	Springs. All new spring construction and/or modifications to existing springs must meet the following minimum requirements:

i.	A watertight wall must completely surround the spring and be at least 18 inches above the highest point off the ground and extending down through the overburden to water-bearing stratum. The top of the surrounding wall must be constructed in such a manner as to accommodate a cover.

ii.	A tight-fitting, locked cover must be installed on top of the encircling wall to protect against contamination or vandalism.

iii.	Where the spring is protected by a springhouse, the building must be rodent and insect-proof and must be kept locked.

iv.	A ditch, or ditches, must be dug to divert surface waters away from the spring. These ditches must be maintained free of debris that would interfere with proper diversion of surface water.

b.	Drilled wells. Drilled wells must be properly located with reference to surrounding sanitary conditions, properly developed, and protected against contamination. Drilled wells must meet the following minimum requirements:

i.	The drilled well must be sealed watertight to the depth necessary to prevent surface contamination, and to seal off contamination from undesirable strata.

ii.	The top of the well casing must be at least 18 inches above ground level, unless otherwise protected.

iii.	A sanitary seal must be installed at the joint where the discharge pipe passes through the well casing.

iv. 	A sanitary seal well cap, vented with a screen, must be installed on top of the well casing.

c.	Dug wells or driven well points. Dug wells or driven well points in shallow aquifers are not recommended as sources of water. If these are in use, then they must meet the following minimum requirements:

i.	Dug wells and driven well points must be properly constructed according to good sanitary engineering practices and protected against potential contamination.

ii.	Dug wells and driven well points must have a watertight lining extending at least six feet below the ground surface. Dug wells must be back filled with clay from the ground surface to a depth of not less than four feet.

- Groundwater under the Influence of Surface Water. Any source meeting the definition of surface water (or groundwater under the influence of surface water) must comply with Section 7(H) of this rule and 40 CFR Sections141§.70, 141.170, 141.500, and 141.700. New dug wells are considered surface water sources. Springs, well points and drilled wells may be classified as surface water, based on testing requirements, as defined above.

## SECTION 4: OPERATION, MAINTENANCE AND DISINFECTION

## A.	Water Pressure

All community water systems must be operated and maintained to provide minimum positive pressure of 20 p.s.i. at the curb stop (curb cock), except as otherwise provided for in limited service agreements.

## B.	Covered Reservoirs

All finished water reservoirs must be covered and the vents to the reservoirs must be adequately screened. Variances to this sub-section are not allowed.

## C.	Flushing

1.	Newly constructed water distribution mains and finished water storage facilities must be flushed and disinfected before use in accordance with the appropriate AWWA standard (See Section (3)(F)(2) of this rule).

2.	No spring basin, collecting basin, well, infiltration gallery, water main, pump, standpipe or reservoir may be placed in service following cleaning or repairs until it has been properly disinfected.

## D.	Disinfection

## When any water system fails to meet the applicable requirements of the Revised Total Coliform Rule (78 FR 10269, February 13, 2013 as amended at 79 FR 10665 February 26, 2014) and/or fails to produce other microbiological test results that indicate microbiological safety from fecal contaminants, the Department may designate the disinfectant residual or application rate to be maintained by the system. The Department may require public water systems with ground water sources to be disinfected. Disinfection residual compliance measurements may be accomplished by use of a N. N diethyl-p-phylenediamine (DPD) colorimetric test kit or any other method as approved by the Department. All treatment techniques must be approved by the Department prior to the installation.

## E.	Separations and Crossings of Water Mains and Sewers

1.	Water mains must be laid at least 10 feet horizontally from any existing or proposed sewer measured edge to edge. In cases where it is not practical to maintain a ten-foot separation, such as in the case of right-of-way limitations, the Department may allow a waiver to this requirement on a case-by-case basis, if supported by data from the design engineer.

2.	Water mains crossing sewers must be laid to provide a minimum vertical distance of 18 inches of free earth between the water main and the sewer. This requirement applies where the water main is either above or below the sewer. At crossings, one full length of water pipe must be located so both joints will be as far from the sewer as possible. Special structural support for the water and sewer pipes may be required. In such crossings, the Department may require sewer pipe of like material as the water pipe, plus concrete encasement.

3.	There must be at least a 10-foot horizontal separation between water mains and existing or future sanitary sewer force mains. There must be an 18-inch vertical separation at crossings, as required in Section (4)(E)(2) of this rule.

4.	No water pipe may pass through or come in contact with any part of a sewer manhole.

## F.	Cross-Connection

Public water systems must comply with the applicable provisions of Maine’s Cross-Connection Rules (10-144 CMR Ch. 226) and Maine’s Internal Plumbing Code (02-395 CMR Ch. 4) and are incorporated by reference.

G.	Hydrants

All new or replacement hydrants must either contain no drain or must have the drain plugged prior to installation. The barrels of the hydrants must be pumped dry during freezing weather or protected with propylene glycol or food safe glycerin.

## H.	Curb Stops

Curb stops (curb cocks) for new or replacement installations must be of the type manufactured with pluggable drains and plugged or without drain holes.

## I.	Emergency Changes

1.	The supplier of water must not take, use, or cause to be taken for use, water from any alternate source or change other treatment processes which involve the addition or deletion of any chemicals, without the approval of the Department. The Department will advise the supplier of water and interested local officials of the approved action or proposed action by the supplier of water to protect the public health. If there is no person from the Department available at the time of an emergency, such action will be taken only by a designated operator, licensed by the Board of Licensure of Water System Operators, who must notify the Department at the earliest possible business hour.

2.	A printed copy of this section must be conspicuously posted by the supplier of water and must be readily available to any water system operator. Such posting must include the address and phone number of the Department.

## J.	Fluoridation

1.	Authorization: In those municipalities which have authorized the addition or discontinuation of fluoride to their water supply pursuant to 22 MRS §2653, the municipal clerk must inform the water system in writing of the municipality’s authorization, within 10 days of the final tabulation by the Secretary of State, pursuant to 22 MRS§2656(3). The water system must inform the Department in writing within seven days of the public water system receiving such notice from the municipal clerk.

2.	Optimum Level: The target level of fluoride for dental benefit is 0.7 milligrams per liter (mg/l) in drinking water in Maine.

3.	Recommended Control Range: The recommended control range is 0.5 to 1.2 mg/l (parts per million) of the optimum level. The recommended control range helps maintain optimal fluoridation.

4.	Monitoring: All public water systems that fluoridate must monitor the daily fluoride concentration at each application on days in which fluoride is added. The measurement at the fluoride application point must be performed by an accepted analytical method. Theoretical calculations have value as a quality control measure and can be substituted in the event of analytical method malfunction, not to exceed 10 days in a month.

5.	Daily Analytical Measurement: Public water systems that measure for a daily analytical must continuously monitor for fluoride ion concentration at each fluoride application point, unless the conditions of Section 4(J)(5)(b) are met. Automated continuous monitoring must include or meet the following:

a.	Continuous monitors may adapt a specified fluoride testing methodology, provided the chemistry, precision and accuracy are equal to or greater than the original testing methodology. See Section 7(C)(3) for testing methodology requirements. Calibration must be according to manufacturer’s recommendations.

b.	Instrumentation providing for notification of water operator if fluoride concentration is outside of optimum range.

c.	Instrumentation providing for notification of water operator if there is a failure of the continuous monitoring.

d.	In lieu of continuous monitoring, a representative daily grab sample(s) may be collected from each fluoridation application point and analyzed daily for fluoride ion concentration.

e.	If the result of a fluoride analysis is outside the optimum range, the sampling and measurement must be confirmed by re-sampling as soon as practicable. If re-sampling confirms the result, the reason will be corrected and documented on monitoring records.

i.	If the repeat sample is greater than 2.0 mg/l, the operator must take appropriate action to correct the problem and inform the Department within 72 hours.

ii.	If the repeat sample is less than 0.5 mg/l, then the operator must correct the problem.

6.	Daily Analytical Samples:

a.	If the daily analytical measurements or substituted theoretical calculations are outside the optimum range (0.5 to 1.2 mg/l) for more than 10 days during the month, then the public water system must notify the Department of the intended course of action to address quality assurance.

b.	In addition to the daily monitoring requirements, a monthly compliance sample of fluoridated water from the distribution system must be submitted at least once each month to a laboratory certified to analyze fluoride. The Department may require additional testing, based on sample results and compliance history.

7.	Temporary Suspension of Fluoride: If a public water system suspends the addition of fluoride for more than 30 consecutive days, then the public water system must provide public notification as soon as practicable, or within 30 days, whichever is sooner, with appropriate public notification language. Modifications to the following text must be approved by the Department. The following language is acceptable language for the public water system to distribute to customers in the event of any temporary suspension of fluoride:

8.		PUBLIC NOTIFICATION

TEMPORARY FLUORIDATION SUSPENSION

Dear User, The fluoridation adjustment in your community drinking water will be (or has been) temporarily suspended due to: (                      ). Fluoridation is scheduled to be restored by the following date: (                      ).

9.	Compliance Sample Results: Based upon the analytical results from a certified laboratory, the following table will be used to determine the necessary action.

Fluoride Level	Action

| < 0.5 or > 1.2 mg/l for two consecutive months. | Post Public Notice in Consumer Confidence Report |
| --- | --- |
| > 2.0 mg/l and ≤4.0 mg/l | Post federal secondary contaminant public notice in Consumer Confidence Report |
| > 4.0 mg/l | Tier 2 violation: Post public notice within 30 days |

10.	Use of Consumer Confidence Report /Public Notification Language: Failure to Monitor: If a public water system fails to collect any compliance sample(s), the public water system must provide public notification of the failure to monitor or report in the annual Consumer Confidence Report.

a. 	The following statement must be included in the public water system’s annual Consumer Confidence Report:

i. 	Fluoride monitoring/reporting violations: The public water system must state the following: In (identify reporting period), our water system failed to test and report monthly fluoride results to the State of Maine Drinking Water Program. Fluoride levels must be maintained between 0.5 to 1.2 mg/l, for those water systems that fluoridate the water.

ii. 	Fluoride compliance samples outside optimum range of 0.5 – 1.2 mg/l for two consecutive months: The public water system must state the following: During (identify months out of range), our water system failed to report fluoride levels within the optimum range of 0.5 to 1.2 mg/l. The following steps have been taken to address this problem (insert description of the action taken).

b. 	Public water systems that have temporarily taken their fluoridation off-line due to malfunctions or maintenance are not required to collect and report a compliance sample while fluoridation equipment is off-line.

## K.	Bottled Water

Public water systems which bottle water for consumption must comply with this section and any other relevant section of this rule.

- Ongoing Water Quality Monitoring/Reporting for Bottled Water Facilities

a.	General requirements. All plants producing bottled water must be responsible for sampling and testing for all physical, chemical, microbiological and radiological parameters specified in Appendix A of this rule. Water quality results must be reported below all maximum contaminant levels set within Appendix B.

i.	Analyses must be conducted by a certified laboratory in accordance with the testing and methodological requirements specified by the National Primary Drinking Water Regulations (40 CFR Sections 141-143).

ii.	Raw samples from each source must be analyzed by a certified laboratory as often as necessary, to identify evidence of any change in water quality, but at a minimum frequency of quarterly, for total coliform bacteria and annually for chemical, physical, and radiological contaminants, which are listed in Appendix A of this rule.

iii.	Finished water (production water) monitoring frequency will be determined by the Department, based on raw water quality results, treatment, and deficiencies identified.

b.	Reduced testing for bottled water facilities: The Department may reduce the frequency of water quality testing requirements on a case-by-case basis, after reviewing the source conditions and water quality results for each source and determining no potential health risks. The Department also reserves the right to reduce the monitoring frequency of post-treated water after determining no potential health risks from water quality results.

c.	 Testing for bottled water facilities: Notwithstanding any other provision of this rule, the Department may require any bottler, distributor or vendor of bottled water to test and submit results to the Department for any substance at any time, when the Department determines that the substance may be present in a water source and may threaten public health. The Department reserves the right to increase testing/monitoring frequency, based upon an evaluation of geologic conditions, individual land use and other factors potentially affecting water quality.

d.	Cease production orders: When there is a violation of this rule, or when, in the judgment of the Department, a condition exists in a public water system which will cause a violation and potentially cause a serious risk to public health, the Department may require the bottler to cease water production. This order may occur in response to one of the following events:

i.	Confirmed E. coli in the source water without meeting 4-log virus inactivation, including a detectable chlorine residual;

ii.	Bottled water after treatment and prior to bottling which contains a drinking water contaminant exceeding the maximum contaminant level within this rule

iii.	An unprotected direct cross-connection with the sanitary sewer; or

iv.	Any other violation that poses a potential imminent threat to public health, as determined by the Department.

## L.	Sanitary Surveys

  - 1.	The following public water systems must have a sanitary survey conducted by the Department no less frequently than every three years:

  - a.	Community Water Systems

  - i.	The Department reserves the right, based on 40 CFR Parts 141 and 142, to conduct some community sanitary surveys every five years.

  - ii.	If the Department determines that a community public water system will receive a sanitary survey every five years, it will notify the public water system in writing of this change.

  - b.	Bottled water systems, referred to in Section 4(K) of this rule.

  - c.	Noncommunity Water Systems with a surface water source, or with a source of groundwater under the direct influence of surface water, as defined in Section 1(B)(34) of this rule.

  - 2.	Non-community water systems other than those in Section 4(L)(1)(c)must have a sanitary survey conducted no less frequently than once every five years.

  - 3.	Sanitary surveys address the following eight components as part of the on-site process:

a.	Evaluation of the source and protective measures in place to ensure acceptable quality and quantity;

b.	Evaluation of the treatment processes in place to ensure adequate water quality;

c.	Evaluation of the distribution system;

d.	Evaluation of the finished water storage facilities, including quantity;

e.	Evaluation of pumps, pump facilities and controls;

f.	Review of monitoring and reporting results and the data verification process;

g.	Evaluation of system management practices and operations; and

h.	Review of operator certification or licensure for compliance with Rules Relating to the Licensure of Water System Operators (90-429 CMR Ch. 1).

4.	During all sanitary surveys, the following parties must be present:

a.	Public water system administrative contact or other management personnel;

b.	For any public water system required to designate a licensed water operator, one or more licensed designated operators; and

c.	Any other individuals determined by the Department to be required.

5.	If a public water system is required to prepare a disinfection profile under the requirements of the Enhanced Filtration and Disinfection Rules (10-144 CMR Ch. 231, Section 7(N); 40 CFR 141.170 § Subpart (P)), the profile must be reviewed as part of the sanitary survey.

6.	If a significant deficiency is identified in the sanitary survey report, the public water system must report to the Department within 45 days of receipt of the report an explanation how the public water system will address the deficiency and when the repairs will occur.

7.	If a public water system is required to develop a disinfection profile, then the public water system must consult with the Department prior to making any significant change to its disinfection practice. The term any significant change may include, but is not limited to, any of the following:

a.	Changes to the point of disinfection addition;

b.	Changes to the disinfectant used in the treatment process;

c.	Changes to the disinfectant process; or

d.	Any other modification identified by the Department.

8.	For public water systems serving ground water to a population less than 1,000, the Department’s sanitary surveys will evaluate the appropriateness of the public water system’s monitoring schedule. The Department may modify these particular monitoring schedules, as necessary, based on historical water quality testing results, or if changes in the number of, and/or location of, potential sources of contamination are identified during the sanitary survey.

9.	The Department may identify sanitary defects during a sanitary survey under the Revised Total Coliform Rule at Section 7(Y). If the public water system fails to correct such sanitary defects within the time frame set, then the Department will rescind any reduced monitoring status held by the PWS.

M.	Ongoing Water Testing Requirements for Water Vending Machines

1. 	Pursuant to 22 MRS §2613(3), a bacteriological sample of a water vending machine must be submitted to the Department at least every three months.

2.	If the water vending machine reports at least one year of clean results (i.e. no coliform bacteria contamination), then the Department may reduce the frequency of sampling to one sample per year.

N.	Tanks and Clearwells: repairs, coating, painting of surfaces touching finished water

1.	Public water systems with new water storage tanks poured in place or constructed on site must test for volatile organic compounds (VOCs) and report results below all maximum contaminant levels before such tanks are placed into service.

2.	Public water systems with coated or painted tanks must test for VOCs and report results below all maximum containment levels to the Department before being placed into service.

3.	Repairs or changes requiring a petroleum-based chemical to be used for tanks, requires a VOC test with results below all maximum contaminant levels before such tanks may be placed back into service.

# SECTION 5: RECORD MAINTENANCE

The owner or operator of a public water system must retain certain records on the public water system premises, or at a convenient location near the premises. Such records (indicated below) must be made available to the public or the Department during an inspection for their review, upon request.

## A.	Water Analyses

1.	Records of bacteriological analyses made pursuant to this rule must be kept for not less than five years. Records of chemical analyses made pursuant to this rule  must be kept for not less than 10 years except for lead and copper analyses, which must be kept for 12 years. Actual laboratory reports may be kept, or data may be transferred to tabular summaries, provided that the following information is included:

a.	Name of public water system and public water system ID number (PWSID);

b.	The date, place, and time of sampling and the name of person who collected the sample;

c.	Identification of the sample as to location and type; as to whether it was a routine distribution system sample, check sample, raw process water sample, or other special purpose sample;

d.	Date and time that lab received sample;

e.	Date and time of analysis;

f.	Laboratory and person responsible for performing analysis;

g.	The analytical technique/method used;

h.	Minimum detection limits (MDL); and

i.	The results of the analysis with, where appropriate, the units of measurement.

2.	Certified laboratories must submit results to the Department in a format approved by the Department, which includes hard-copy or electronic forms.

3.	Records of lead analyses and of copper analyses made pursuant to this rule, as pertinent to requirements of the National Primary Drinking Water Regulations (40 CFR Part 141, Subpart I (Control of Lead and Copper)), incorporated by reference at Section 7(I) of this rule, must be kept for not less than 12 years.

B.	Violations

Records of action taken by the system to correct violations of any drinking water rule must be kept for a period of not less than three years after the last action taken with respect to the particular violation involved.

## C.	Sanitary Surveys

Copies of any written reports, summaries, or communications relating to sanitary surveys of the public water system conducted by the system itself, by a private consultant, or by any local, State, or federal agency, must be kept for a period of not less than 10 years after completion of the sanitary survey involved.

## D.	Variances and Exemptions

Records concerning a variance or exemption granted to the public water system must be kept for a period ending not less than five years following the expiration of said variance or exemption.

## E.	Operational Records

Each public water system must maintain operational records, which must be available for inspection and review by the Department and the public. Operational records must be maintained for at least five years. Operational records include any information necessary to ensure proper oversight of the public water system.

        - Assessments Required By the Revised Total Coliform Rule

Public water systems must maintain copies of any assessment forms documenting assessments performed, as required by the Department and in accordance with the Revised Total Coliform Rule (40 CFR Part 141, Subpart Y and Section 7(Y) of this rule), along with records of any associated corrective actions, for five (5) years after completion of the assessment or the corrective action.

# SECTION 6: REPORTING REQUIREMENTS

A person who owns or operates a public water system (or a laboratory certified/accredited in the State of Maine) is authorized and required to report the following items and events to the Department or Certified Laboratories:

## A.	Failure of a Public Water System to Comply With the Drinking Water Rule

All public water system owners or operators must report any failure to comply with applicable drinking water rules and regulations directly to the Department, including any failure to monitor or report water analyses within required timeframes outlined in 40 CFR 141, Subpart Q, unless the Department performed the analysis and reported the results.

## B.	Submission of Water Quality Samples to a Certified Laboratory

## All public water system owners or operators must submit water samples to a certified laboratory for analysis.

## C.	Analysis Reporting to the Department

1.	Public water system owners or operators must ensure the submission of sample results and compliance operational data to the Department in the format specified by the Department.

2.	Unless a shorter period is specified, the results of tests, measurements, and analyses required by Sections 7, 8 and 9 of this rule must be reported to the Department by the tenth day of the month following the month in which the samples were required to be collected.

3.	Certified laboratories must report the following results to the Department within one business day of the results being discovered:

a.	Positive total coliform results;

- Arsenic results greater than 0.05 mg/L.

c.	Lead results greater than 0.1 mg/L.

4.	Certified laboratories must report the following results for acute contaminants to the Department on the same day that the results are known:

a.	E. coli positive results;

b.	Nitrate exceedances of the maximum contaminant level; and

c.	Nitrite exceedances of the maximum contaminant level.

5.	All reports of laboratory analyses for compliance purposes must be submitted to the Department by the certified laboratory contracted by the public water system to analyze the samples. Any portion of the analysis sub-contracted to another accredited laboratory must be reported by the primary contracted laboratory. The primary contracted laboratory must submit the final report to the Department.

6.	Certified laboratories must submit forms to the Department in a format approved by the Department, which includes hard-copy or electronic submission.

7.	The Department may require any bottler, distributor, or vendor of bottled water to test and submit results to the Department for any substance at any time, when the Department has reason to believe that the substance may be present in a water source and may threaten public health. The Department reserves the right to increase testing/ monitoring frequency, based upon the potential health risk.

## D.	Public Water Systems Directly Submitting Operational Reports to Department

1.	Each community system serving municipalities and/or Districts must file a monthly operational report with the Department no later than the tenth day of each month. The reports must be made on forms provided or approved by the Department and include but are not limited to: records of daily test results, daily water production and usage, daily chemical usage, any change in normal treatment procedure, and other pertinent information as directed by the Department.

2.	All public water systems not included in Section (6)(D)(1) of this rule that add chemicals on a continuous basis must submit monthly reports on forms provided or approved by the Department or via electronic means, as approved by the Department. These monthly reports must be submitted to the Department no later than the tenth day of each month and must include the following: records of daily test results, daily chemical usage, any change from the normal treatment procedure, and any other pertinent information. Based upon the complexity, size, and the public water system’s compliance history, the Department may reduce a public water system’s daily monitoring requirements, but in no case shall the frequency of reporting be reduced to less than twice per week.

3.	If a designated operator is required to oversee a public water system that submits operational records to the Department, then the designated operator is required to sign all such records. In some limited circumstances, such as with large municipal public water systems, the Department may authorize the designated operator to delegate an agent to sign the records.

4.	All water utilities regulated by the Maine Public Utilities Commission and bottled water facilities must submit water withdrawal records to the Department at least annually but may report more frequently.

## E.	Change in Ownership

## New owners of community and non-transient, non-community public water systems must notify the Department within 60 days of the change in ownership.

## F.	Security Reports

Public water system owners must notify the Department and law enforcement officials immediately to report any act of potential or suspected tampering. Any security situation where the public water system contacts law enforcement officials must also be reported to the Department.

SECTION 7: NATIONAL PRIMARY DRINKING WATER REGULATIONS

(40 CFR CHAPTER I, SUBCHAPTER D, PART 141)

Title 40 CFR. Section 141.6, published July 2024, is hereby incorporated herein by this reference.

# A. 	General Provisions

# 1.	Applicability

# Title 40 Code of Federal Regulations (CFR), Subpart A, §§ 141.1-141.6, last amended July 1, 2024.

2.	Definitions

Title 40 CFR Section 141.2, published July 1, 2024, is hereby incorporated herein by this reference, with the exceptions, additions or changes as set forth below.

Act means the Maine Water for Human Consumption Act at 22 Maine Revised Statutes, Chapter 601. This definition of Act only applies to Section 7 of this rule.

Administrator means the Commissioner of the Department of Health and Human Services or the designated representative thereof.

Person means person, as defined in Section 2 of this rule.

Public water system means a public water system as defined in Section 2 of this rule.

State means the State of Maine.

3.	Coverage

Title 40 CFR Section 141.3, published July 1, 2024, is hereby incorporated herein by this reference.

4.	Variances and exemptions

Title 40 CFR Section 141.4, published July 1, 2024, is hereby incorporated herein by this reference.

5.	Siting requirements

Title 40 CFR Section 141.5, published July 1, 2024, is hereby incorporated herein by this reference.

## 6.	Effective dates

## B.	Maximum Contaminant Levels

Title 40 CFR Ch. I, Subchapter D, Part 141, Subpart B, §§ 141.11-141.13, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections establish maximum contaminant levels for arsenic & nitrate (Section 141.11) and turbidity (Section 141.13).).

Additional maximum contaminant levels are contained in Subpart F, §§ 141.50-141.55; Subpart G, §§ 141.60-141.66; and in Appendix B at the end of Section 7 of this Rule.

## C.	Monitoring and Analytical Requirements

Title 40 CFR Ch. I, Subchapter D, Part 141, Subpart C, §§ 141.21 through 141.29, last amended July 1, 2024, and Subpart Y, §§ 141.851 through 861 are hereby incorporated herein by this reference.

These sections contain:

- Monitoring and analytical requirements for the following contaminants:

  - Coliform bacteria (141.21 and additional requirements under Subpart Y, Section 141.851  through 861).

  - Turbidity (141.22).

  - Inorganic chemicals (141.23).

  - Organic chemicals (volatile and synthetic compounds) (141.24).

  - Radionuclides (141.25-26).

- Alternate analytical techniques (141.27).

- Requirements applicable to certified laboratories (141.28).

- Requirements applicable to consecutive public water systems (141.29).

- Appendix A to Subpart C of Part 141 - Alternative Analytical Methods/Techniques.

Additionally, the following State monitoring and reporting requirements for community and non-transient non-community water systems include;

- State monitoring and analytical requirements for methyl tertiary-butyl ether for community and non-transient non-community water systems.

  - The sampling frequency for methyl tertiary-butyl ether for community water systems and non-transient non-community water systems must be the same as outlined at Section 7(C)(1)(d) above and 40 CFR §141.24 for volatile organic contaminants (VOCs). MTBE monitoring will begin with the next compliance period for VOCs in accordance with the system’s VOC testing schedule.

  - The analytical method utilized to test for methyl tertiary-butyl ether must be EPA Drinking Water Method 524.

- State monitoring and analytical requirements for velpar/hexazinone for community and non-transient non-community water systems.

  - The sampling frequency for velpar/hexazinone for community water systems and non-transient non-community water systems must be the same as outlined at Section 7(C)(1)(d)above and 40 CFR §141.24 for semi-volatile organic contaminants (SVOs). Velpar/hexazinone monitoring will begin with the next compliance period for SVOs in accordance with the system’s VOC testing schedules.

  - The analytical method utilized to test for velpar/hexazinone must be EPA Drinking Water Method 525.

## D.	Reporting, Public Notification and Record Keeping

Title 40 CFR, Chapter I, Subchapter D, Part 141, Subpart D, Sections 141.31 through 141.35, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain reporting and record keeping requirements, as well as requirements for  reporting unregulated contaminant monitoring results.

Additionally:

- State reporting requirements for MtBE and Velpar/hexazinone.

  - The supplier of water must submit results of tests, measurements, or analyses to the Department for methyl tertiary-butyl ether and for velpar/hexazinone in accordance with Sections 6(B) and 7(D)(1)(a) of this rule. The reporting requirements are the same as that set for volatile organic contaminants.

  - State reporting for MTBE & Velpar/Hexazinone.

i.	The owner or operator of a public water system must complete public notification for any failure to monitor or exceedance of the MCL for methyl tertiary-butyl ether or velpar/hexazinone. Public notification must be completed with the same form, manner, and frequency as required by the provisions for volatile organic contaminants or synthetic organics, accordingly, at 40 CFR Part 141, Subpart Q. The mandatory health effect language as specified at Section 7(D)(1)(b)(ii) of this rule for methyl tertiary-butyl ether or Section 7(D)(1)(b)(iii) for velpar/hexazinone is to be placed in the public notification for any exceedance of the methyl tertiary-butyl ether or velpar/hexazinone MCL.

ii.	Mandatory health effect language for methyl tertiary-butyl ether:

The State of Maine has set an enforceable drinking water standard (MCL) for methyl tertiary-butyl ether known as MTBE. MTBE generally contaminates drinking water from leaking underground fuel tanks and accidental spills. This chemical has been shown to have adverse effects on laboratory animals after long term exposure to high levels. Chemicals which cause adverse effects in laboratory animals may also cause adverse effects in humans who are exposed at lower levels over long periods of time. The Department has set an enforceable drinking water standard for MTBE of 35 parts per billion to reduce the risk of adverse effects which have been observed in animals. Drinking water which meets this standard is associated with little to no risk and should be considered safe for human consumption.

iii.	Mandatory health effect language for velpar/hexazinone:

The State of Maine requires testing for velpar/hexazinone for water sources near blueberry fields (where the chemical may be applied). This chemical is known to be a severe eye irritant. This chemical is not a known human carcinogen and does not cause other toxic effects of concern. The EPA has set a lifetime health advisory (HA) level of 0.21 mg/L or 200 ug/L for this compound. The Department requires monitoring to ensure levels in drinking water supplies do not exceed the health advisory limit.

c.	State required record maintenance for MtBE & Velpar/hexazinone

Any owner or operator of a public water system must retain on its premises, or a convenient location near its premises, the records of analyses for methyl tertiary-butyl ether and/or velpar/hexazinone in the same form, manner, and frequency as that required for the volatile organic contaminants or synthetic organic contaminants at 40 CFR §141.33 and as incorporated by reference in this rule at Section 7 above.

E.	Special Regulations, Including Monitoring Regulations and Prohibition on Lead Use

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart E, Sections 141.40 through 141.42, last amended July 1, 2024, are hereby incorporated herein by this reference.

- Special monitoring for unregulated contaminants (141.40).

- Special monitoring for sodium (141.41).

- Special monitoring for corrosivity characteristics (141.42).

F. 	Maximum Contaminant Level Goals and Maximum Residual Disinfectant Level Goals

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart F, Sections 141.50 through 141.55, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections provide the maximum contaminant level goals and the maximum residual disinfectant level goals for the following contaminants and disinfectants.

- Maximum contaminant level goals for organic contaminants (141.50).

- Maximum contaminant level goals for inorganic contaminants (141.51).

- Maximum contaminant level goals for microbiological contaminants (141.52).

- Maximum contaminant level goals for disinfection byproducts (141.53).

- Maximum residual disinfection level goals for disinfectants (141.54).

- Maximum contaminant level goals for radionuclides (141.55).

- Maximum contaminant level goals for per- & poly-fluoroalkyl substances (141.50).

## G.	National Revised Primary Drinking Water Regulations: Maximum Contaminant Levels and Maximum Residual Disinfectant Levels

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart G, Sections 141.60 through 141.66, last amended July 2024, are hereby incorporated herein by this reference.

These sections provide the maximum contaminant levels and the maximum residual disinfectant levels for the following contaminants and disinfectants. Appendix B lists the primary, secondary and unregulated contaminant levels for all drinking water standards.

- Effective dates (141.60).

- Maximum contaminant levels for organic contaminants (141.61).

- Maximum contaminant levels for inorganic contaminants (141.62).

- Maximum contaminant levels (MCLs) for microbiological contaminants (141.63).

- Maximum contaminant level for methyl tertiary-butyl ether (MTBE) in community and non-transient non-community water systems.

  - The maximum contaminant level for methyl tertiary-butyl ether is applicable to both community water systems and non-transient non-community water systems.

  - The maximum contaminant level for methyl tertiary-butyl ether is 35 parts per billion.

  - The best technology, treatment technique or other means available for achieving compliance with the maximum contaminant level for methyl tertiary-butyl ether must be either: the Best Available Technologies (BATs) established by the United States Environmental Protection Agency, or, in the interim, technologies approved by the Department.

- Maximum contaminant levels for disinfection byproducts (141.64).

- Maximum residual disinfectant levels (141.65).

- Maximum contaminant levels for radionuclides (141.66).

- Maximum contaminant levels for per- & poly-fluoroalkyl substances (141.61).

## H.	Filtration and Disinfection

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart H, Sections 141.70 through 141.76, last amended April 2024, are hereby incorporated herein by this reference.

These sections contained in Subpart P, Sections 141.170 through 141.175; Subpart T, Sections 141.500 through 141.571; and Subpart W, Sections 141.700 through 141.723, hereby incorporated by reference.

The Department may require other filtration technologies to meet the combined and/or individual filtration turbidity requirements of conventional or direct filtration, as detailed in Title 40 CFR  Sections 141.550 through 141.571. Failure to meet these turbidity requirements may result in re-evaluation of the previously approved log-removal credit. The Department may grant exceptions to other filtration technologies that were approved, based upon higher turbidity limits.

For public water systems with other filtration technologies that include a clarification process prior to filtration; the Department may require removal of additional total organic carbon (TOC), similar to the requirements for conventional filtration technologies, at 40 CFR § 141.135, if, during any quarter, compliance sample results for total trihalomethanes (TTHM) and/or haloacetic acids (HAA5) exceed their respective MCLs. The public water system may be triggered into a minimum of 12 months of TOC removal testing (to include a source water TOC, source water alkalinity, and a finished water TOC), along with additional treatment or operational modifications, as required by the Department.

## I.	Control of Lead and Copper

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart I, Sections 141.80 through 141.91, last amended 2007, are hereby incorporated herein by this reference.

These sections contain the requirements for lead/copper testing and criteria for addressing action level exceedances.

## J.	Use of Non-Centralized Treatment Devices

Title 40 CFR, Chapter I, Subchapter D, Part 141, Subpart J, Sections 141.100 through 141.101, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain regulations applicable to the use of point-of-use devices and the use of bottled water for MCLs.

## K.	Treatment Techniques

Title 40 CFR, Chapter I, Subchapter D, Part 141, Subpart K, §§Sections 141.110-141.111, last amended April 2024, are hereby incorporated herein by this reference.

These sections contain the requirements and treatment techniques for systems that use acrylamide or epichlorohydrin.

## L.	Disinfectant Residuals, Disinfectant Byproducts and Disinfection Byproducts Precursors

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart L, Sections 141.130 through 141.135, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain the monitoring and analytical requirements and treatment techniques for disinfectant residuals, disinfection by-products, and disinfection by-product precursors.

## M-N.	[Reserved]

## O.	Consumer Confidence Reports

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart O, Sections 141.151 through 141.156 Appendix A, last amended July 1, 2024, are hereby incorporated herein by this reference.

This rule requires community water systems must deliver annual consumer confidence reports to the persons served by their water system, pursuant to 22 MRS §2615-A.

## P.	Enhanced Filtration and Disinfection – Systems Serving 10,000 or More People

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart P, Sections 141.170 through 141.175, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain additional enhanced filtration requirements and disinfection profiling for larger surface water systems (≥10,000 people).

## Q.	Public Notification of Drinking Water Violations

Title 40 CFR Chapter I, Subchapter D, Part 141, Sections 141.201 through 141.211 and Appendices A, B & C, last amended July 1, 2024, are hereby incorporated herein by this reference with the exceptions, additions or changes as set forth below.

Tier 3 Public Notice – Form, manner, and frequency of notice

Title 40 CFR, Section 141.204, last amended July 1, 2024, is hereby incorporated herein by this reference, except that non-community public water systems must provide Tier 3 public notification to the public within 30 days of learning of the violation or situation. A copy of the public notification and certification statement must be provided to the Department within 10 days after providing completing initial or repeat notice to the public.

These sections contain public notification requirements for Tier 1, Tier 2 and Tier 3 violations. This includes special notice for exceedance of the secondary MCL (SMCL) for fluoride, special notice for nitrate exceedances, special notice for failure to complete Cryptosporidium testing and for unregulated contaminant monitoring results.

R.	[Reserved]

## S.	Ground Water Rule

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart S, Sections 141.400 through 141.405, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain the analytical, monitoring and treatment technique requirements for groundwater systems.

## T.	Enhanced Filtration and Disinfection – Systems Serving Fewer Than 10,000 People

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart T, Sections 141.500 through 141.571, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain additional enhanced filtration requirements and disinfection profiling requirements for smaller surface water systems (<10,000 people).

## U.	Initial Distribution System Evaluations

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart U, Sections 141.600 through 141.605, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain the initial distribution system evaluations requirements applicable to systems transitioning to Stage 2 Disinfection Byproducts.

V.	Stage 2 Disinfection Byproducts Requirements

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart V, Sections 141.620 through 141.629, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections contain the additional disinfection byproducts monitoring requirements and operational evaluation levels under Stage 2 of the Disinfection Byproducts Rules (DBPR).

W.	Enhanced Treatment for Cryptosporidium

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart W, Sections 141.700 through 141.723, last amended July 1, 2024, are hereby incorporated herein by this reference.

These sections establish and extend treatment technique requirements for Cryptosporidium in lieu of maximum contaminant levels.

X.	[Reserved]

Y.	Revised Total Coliform Rule

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart Y, Sections 141.851through 141.861, last amended July 1, 2024, are hereby incorporated herein by this reference with the exceptions, additions or changes as set forth below.

- Routine monitoring requirements for non-community water systems serving 1,000 or fewer people using only ground water (Section 141.854). Seasonal non-community water systems are required to monitor for total coliform on a monthly basis during their annual operation period. Seasonal systems will not be eligible for quarterly monitoring.

- Routine monitoring requirements for community water systems serving 1,000 or fewer people using only ground water (Section 141.855). These community water systems will be moved to monthly monitoring regardless of their status/monitoring frequency was at the time of implementation of the Revised Total Coliform Rule in 2016. Community systems will not be eligible for quarterly monitoring.

- Repeat monitoring and E. coli requirements (Section 141.858). Each system will be required to take a minimum of one set of repeat samples. If the system has already triggered an assessment, it will be at the Department’s discretion whether additional repeat samples are needed.

Z.	Per- & Poly-Fluoroalkyl Substances Requirements

Title 40 CFR Chapter I, Subchapter D, Part 141, Subpart Z, Sections 141.900 through 141.905, last amended July 1, 2024, are hereby incorporated herein by this reference.

SECTION 8: NATIONAL PRIMARY DRINKING WATER REGULATIONS – IMPLEMENTATION (40 CFR CHAPTER I, SUBCHAPTER D, PART 142)

## A.	General Provisions

1.	Applicability

Title 40 CFR Section 142.1, published July 2024, is hereby incorporated herein by this reference.

2.	Definitions. The following definitions only apply to Sections 7 and 8 of this rule.

Title 40 CFR Section 142.2, published July 2024, is hereby incorporated herein by this reference, with the exceptions, additions or changes as set forth below.

Act means the Maine Water for Human Consumption Act at 22 Maine Revised Statutes, Chapter 601.  This definition of Act applies only to this section of the rule.

Administrator means the Commissioner of the Department of Health and Human Services or the designated representative thereof.

Agency means the Maine Department of Health and Human Services.

Indian tribe means a federally recognized Indian tribe within the State of Maine

Public water system means a public water system as defined in Section 2 of this rule.

State means the State of Maine.

3.	Scope

Title 40 CFR Section 142.3, published July 2024, is hereby incorporated herein by this reference.

4.	State and local authority

Title 40 CFR Section 142.4, published July 2024, is hereby incorporated herein by this reference.

## B.	Primary Enforcement Responsibility

1.	Requirements for a determination of primary enforcement responsibility

Title 40 CFR Section 142.10, published July 2024, is hereby incorporated herein by this reference.

2.	Initial determination of primary enforcement responsibility

Title 40 CFR Section 142.11, published July 2024, is hereby incorporated herein by this reference.

3.	Revision of State programs

Title 40 CFR Section 142.12, published July 2024, is hereby incorporated herein by this reference.

4.	Public hearing

Title 40 CFR Section 142.13, published July 2024, is hereby incorporated herein by this reference.

5.	Records kept by States

Title 40 CFR Section 142.14, published July 2024, is hereby incorporated herein by this reference.

6.	Reports by States

Title 40 CFR Section 142.15, published July 2024, is hereby incorporated herein by this reference.

7.	Special primacy requirements

Title 40 CFR Section 142.16, published July 2024, is hereby incorporated herein by this reference.

8.	Review of State programs and procedures for withdrawal of approved primacy Programs

Title 40 CFR Section 142.17, published July 2024, is hereby incorporated herein by this reference.

9.	EPA review of State monitoring determinations

Title 40 CFR Section 142.18, published July 2024, is hereby incorporated herein by this reference.

10.	EPA review of State implementation of national primary drinking water regulations for lead and copper

Title 40 CFR Section 142.19, published July 2024, is hereby incorporated herein by this reference.

## C.	Review of State-Issued Variances and Exemptions

1.	State-issued variances and exemptions

Title 40 CFR Section 142.20, published July 2024, is hereby incorporated herein by this reference.

2.	State consideration of a variance or exemption request

Title 40 CFR Section 142.21, published July 2024, is hereby incorporated herein by this reference.

3.	Review of State variances, exemptions and schedules

Title 40 CFR Section 142.22, published July 2024, is hereby incorporated herein by this reference.

4.	Notice to State

Title 40 CFR Section 142.23, published July 2024, is hereby incorporated herein by this reference.

5.	Administrator's rescission

Title 40 CFR Section 142.24, published at July 2024, is hereby incorporated herein by this reference.

## D.	Federal Enforcement

1.	Failure by State to ensure enforcement

Title 40 CFR Section 142.30, published July 2024, is hereby incorporated herein by this reference.

2.	[Reserved]

3.	Petition for public hearing

Title 40 CFR Section 142.32, published July 2024, is hereby incorporated herein by this reference.

4.	Public hearing

Title 40 CFR Section 142.33, published July 2024, is hereby incorporated herein by this reference.

5.	Entry and inspection of public water systems

Title 40 CFR Section 142.34, published July 2024, is hereby incorporated herein by this reference.

## E.	Variances Issued By the Administrator Under Section 1415 (a) of the Act

1.	Requirements for a variance

Title 40 CFR Section 142.40, published July 2024, is hereby incorporated herein by this reference.

2.	Variance Request

Title 40 CFR Section 142.41, published July 2024, is hereby incorporated herein by this reference.

3.	Consideration of a variance request

Title 40 CFR Section 142.42, published July 2024, is hereby incorporated herein by this reference.

4.	Disposition of a variance request

Title 40 CFR Section 142.43, published July 2024, is hereby incorporated herein by this reference.

5.	Public hearings on variances and schedules

Title 40 CFR Section 142.44, published July 2024, is hereby incorporated herein by this reference.

6.	Action after hearing

Title 40 CFR Section 142.45, published July 2024, is hereby incorporated herein by this reference.

7.	Alternative treatment techniques

Title 40 CFR Section 142.46, published July 2024, is hereby incorporated herein by this reference.

## F.	Exemptions Issued By the Administrator

1.	Requirements for an exemption

Title 40 CFR Section 142.50, published July 2024, is hereby incorporated herein by this reference.

2.	Exemption request

Title 40 CFR Section 142.51, published July 2024, is hereby incorporated herein by this reference.

3.	Consideration of an exemption request

Title 40 CFR Section 142.52, published July 2024, is hereby incorporated herein by this reference.

4.	Disposition of an exemption request

Title 40 CFR Section 142.53, published July 2024, is hereby incorporated herein by this reference.

5.	Public hearings on exemption schedules

Title 40 CFR Section 142.54, published July 2024, is hereby incorporated herein by this reference.

6.	Final schedule

Title 40 CFR Section 142.55, published July 2024, is hereby incorporated herein by this reference.

7.	Extension of date for compliance

Title 40 CFR Section 142.56, published July 2024, is hereby incorporated herein by this reference.

8.	Bottled water, point-of-use, and point-of-entry devices

Title 40 CFR Section 142.57, published July 2024, is hereby incorporated herein by this reference.

## G.	Identification of Best Technology, Treatment Techniques or Other Means Generally Available

1.	Variances from the maximum contaminant level for total trihalomethanes

Title 40 CFR Section 142.60, published July 2024, is hereby incorporated herein by this reference.

2.	Variances from the maximum contaminant level for fluoride

Title 40 CFR Section 142.61, published July 2024, is hereby incorporated herein by this reference.

3.	Variances and exemptions from the maximum contaminant levels for organic and inorganic chemicals and exemptions from the treatment technique for lead and copper

Title 40 CFR Section 142.62, published July 2024, is hereby incorporated herein by this reference.

4.	Variances and exemptions from the maximum contaminant level for total coliform

Title 40 CFR Section 142.63, published July 2024, is hereby incorporated herein by this reference.

5.	Variances and exemptions from the requirements of Part 141, Subpart H - Filtration and Disinfection

Title 40 CFR Section 142.64, published July 2024, is hereby incorporated herein by this reference.

6.	Variances and exemptions from the maximum contaminant levels for radionuclides

Title 40 CFR Section 142.65, published July 2024, is hereby incorporated herein by this reference.

## H.	Indian Tribes

1.	Requirements for Tribal Eligibility

Title 40 CFR Section 142.72, published July 2024, is hereby incorporated herein by this reference.

2	Request by an Indian Tribe for a determination of treatment as a State

Title 40 CFR Section 142.76, published July 2024, is hereby incorporated herein by this reference.

3.	Procedure for processing an Indian Tribe's application for treatment as a State

Title 40 CFR Section 142.78, published July 2024, is hereby incorporated herein by this reference.

## I.	Administrator’s Review of State Decisions That Implement Criteria Under Which Filtration is Required

1.	Review procedures

Title 40 CFR Section 142.80, published July 2024, is hereby incorporated herein by this reference.

2.	Notice to the State

Title 40 CFR Section 142.81, published July 2024, is hereby incorporated herein by this reference.

## J.	[Reserved]

## K.	Variances for Small Systems

## 1.	What is a small system variance?

Title 40 CFR Section 142.301, published July 2024, is hereby incorporated herein by this reference.

2.	Who can issue a small system variance?

Title 40 CFR. Section 142.302, published July 2024, is hereby incorporated herein by this reference.

3.	Which size public water systems can receive a small system variance?

Title 40 CFR Section 142.303, published July 2024, is hereby incorporated herein by this reference.

4.	For which of the regulatory requirements is a small system variance available?

Title 40 CFR Section 142.304, published July 2024, is hereby incorporated herein by this reference.

5.	When can a small system variance be granted by a State?

Title 40 CFR Section 142.305, published July 2024, is hereby incorporated herein by this reference.

6.	What are the responsibilities of the public water system, State and the Administrator in ensuring that sufficient information is available and for evaluation of a small system variance application?

Title 40 CFR Section 142.306, published July 2024, is hereby incorporated herein by this reference.

7.	What terms and conditions must be included in a small system variance?

Title 40 CFR Section 142.307, published July 2024, is hereby incorporated herein by this reference.

8.	What public notice is required before a State or the Administrator proposes to issue a small system variance?

Title 40 CFR Section 142.308, published July 2024, is hereby incorporated herein by this reference.

9.	What are the public meeting requirements associated with the proposal of a small system variance?

Title 40 CFR Section 142.309, published July 2024, is hereby incorporated herein by this reference.

10.	How can a person served by the public water system obtain EPA review of a State proposed small system variance?

Title 40 CFR Section 142.310, published July 2024, is hereby incorporated herein by this reference.

11.	What procedures allow the Administrator to object to a proposed small system variance or overturn a granted small system variance for a public water system serving 3,300 or fewer persons?

Title 40 CFR Section 142.311, published July 2024, is hereby incorporated herein by this reference.

12.	What EPA action is necessary when a State proposes to grant a small system variance to a public water system serving a population of more than 3,300 and fewer than 10,000 persons?

Title 40 CFR Section 142.312, published July 2024, is hereby incorporated herein by this reference.

13.	How will the Administrator review a State’s program under this subpart?

Title 40 CFR Section 142.313, published July 2024, is hereby incorporated herein by this reference.

# SECTION 9: NATIONAL SECONDARY DRINKING WATER REGULATIONS

# (40 CFR CHAPTER I, SUBPART D, PART 143)

## A.	General Provisions

1.	Purpose

Title 40 CFR Section 143.1, published July 2024, is hereby incorporated herein by this reference.

2.	Definitions

Title 40 CFR Section 143.2, published July 2024, is hereby incorporated herein by this reference with the exceptions, additions or changes set forth below.

Administrator means the Commissioner of the Department of Health and Human Services or the designated representative thereof.

Public water system means a public water system as defined in Section 2 of this rule.

State means the State of Maine.

3.	Secondary Maximum Contaminant Levels

Title 40 CFR Section 143.3, published July 2024, is hereby incorporated herein by this reference.

4.	Monitoring

Title 40 CFR Section 143.4, published July 2024, is hereby incorporated herein by this reference.

# SECTION 10: LABORATORY CERTIFICATION

All laboratories performing water testing for compliance purposes for this rule must be certified under the Maine Comprehensive and Limited Environmental Laboratory Accreditation Rule (10-144 CMR Ch. 263), authorized under 22 MRS, §567.

SECTION 11:

RISK AND RESILIENCE ASSESSMENTS,

EMERGENCY RESPONSE PLANS, CYBERSECURITY, AND

EMERGENCY NOTIFICATION PROCEDURES

FOR PUBLIC WATER SYSTEMS

America’s Water Infrastructure Act of 2018 (AWIA) which amends the Safe Drinking Water Act, requires all community public water systems serving more than 3,300 people to develop or update risk resilience assessments and emergency response plans.

All public water systems in Maine must prepare and implement or update existing emergency and security plans to include foreseeable and unforeseeable disturbances relating to production and supply of safe drinking water.

## A.	Emergency Situations

Emergency situations include, but are not limited to the following:

1.	A failure, or significant interruption, in the production of drinking water;

2.	A natural disaster that disrupts the water supply of the public water system;

3.	A chemical spill or biological substance introduced into the public water system’s water source, that increases the potential for contamination;

4.	A cross connection between a potable water supply and a non-potable water supply or harmful substance;

5.	Intentional physical and/or cyber intrusion of the water system;

6.	Any other activity that disturbs the production and supply of safe drinking water to those served by the public water system.

## B.	Risk and Resilience Assessments

1.	All community public water systems serving water to more than 3,300 people were required to conduct a risk and resilience assessment and submit certification of its completion directly to the U.S. EPA by the following deadlines:

a.	March 31, 2020, if the public water system serves water to 100,000 or more people;

b.	December 31, 2020, if the public water system serves 50,000 to 99,999 people; and

c.	June 30, 2021, if the public water system serves water to 3,301 to 49,999 people.

2.	After the initial deadline above is met, each community public water system serving more than 3,300 people must review this assessment at least once every five years, to determine whether the assessment should be revised. Upon completion of this review, the public water system must submit a written certification to the U.S. EPA, attesting that the public water system has completed its review of the assessment and, if applicable, revised it.

3.	Risk and resilience assessments must include the following components:

a.	Description of the risk to the public water system from malevolent acts and natural hazards;

b.	Explanation of the resilience of the pipes and constructed conveyances, physical barriers, source water, water collection and intake, pre-treatment, treatment, storage and distribution facilities, electronic, computer, or other automated systems (including the security of such systems), which are utilized by the public water system;

c.	Description of the monitoring practices exercised by the public water system;

d.	Description of the financial infrastructure of the public water system;

e.	List of any chemical use, storage, or handling performed by the public water system; and

f.	Description of the operation and maintenance protocols performed by the public water system.

## C.	Emergency Response Plans

1.	By 2020 or 2021, depending on the public water system’s customer population size, in accordance with Section 11(B) above, each community public water system serving more than 3,300 people must prepare or revise an emergency plan that incorporates the findings of the risk and resilience assessment.

a.	This emergency response plan must be submitted to U.S. EPA within six months of certifying completion of the risk and resilience plan, referred to in Section 11(B) above.

b.	After the deadline for the risk and resilience deadline is met in Section 11(B) above, each community public water system serving more than 3,300 people must review its emergency response plan at least once every five years, to determine whether the plan should be revised.

i.	This emergency response plan must incorporate any revisions to the risk and resilience assessment.

ii.	Within six months of certifying that the risk and resilience assessment was reviewed, the public water system must also submit certification that the public water system completed its emergency response plan review (and completed revisions, if applicable) to the U.S. EPA.

2.	The emergency response plan must include the following:

a.	Strategies and resources that would improve resilience of the public water system;

b.	Strategies to aid in the detection of malevolent acts or natural hazards that threaten the security or resilience of the public water system.

c.	Plans and procedures that could be implemented, along with an identification of equipment to be used, in the event of a malevolent act or natural hazard that threatens the public water system’s ability to serve and deliver safe water; and

d.	Actions, procedures, and equipment to obviate or significantly lessen the impact of a malevolent act or natural hazard on the public health and the supply and safety of drinking water provided to people, including the development of alternative source water options, relocation of water intakes, and construction of flood protection barriers.

3. 	All community public water systems serving a population of more than 3,300 people in Maine that are required to develop or update an existing emergency response plan must make the plan available for inspection by the Department staff upon request.

## D.	Cybersecurity

## All public water systems must follow Department directives and federal regulations regarding cybersecurity.

## E.	Security Breaches and Emergency Notification Requirements

1.	All public water systems reporting physical and/or cyber security breaches, tampering events or other emergencies affecting water system components to law enforcement must also report the incidents to the Department.

2.	All Public Utilities Commission (PUC)-regulated water systems reporting security-related incidents to law enforcement agencies must report such incidents to both the Department and the PUC.

3.	All public water systems experiencing emergency events involving biological or chemical contamination of water system components must report said events to the Department.

STATUTORY AUTHORITY:

22 MRS §§2611, 2615(5), 2615-A(4), 2617(3), 2618, 2620(2), 2620-C, 2659, 2660-E(1)

EFFECTIVE DATE:

January 13, 1980

AMENDED:

April 20, 1980

June 17, 1981

November 22, 1983

October 29, 1991

January 2, 1993

June 8, 1994

February 6, 1995

August 26, 1995

EFFECTIVE DATE (ELECTRONIC CONVERSION):

May 5, 1996

AMENDED:

June 25, 1998 - Section 7(C,D,G)

June 19, 1999 - Sections 2 (APA, CAPACITY), 3 (A,D,E)

June 20, 2001 - Sections 1-A, Section 7 and 8

June 20, 2001

October 24, 2001

November 4, 2002

August 18, 2003 - Sections 1, 1-B, 2, 3, 4, 6, 11

November 2, 2004 - filing 2004-478

NON-SUBSTANTIVE CORRECTIONS:

February 28, 2005 – minor punctuation and spacing

AMENDED:

September 20, 2006 - filing 2006-410

March 12, 2008 - filing 2008-115

November 30, 2009 - filing 2009-619

February 27, 2012 - filing 2012-51

May 9, 2016 - filing 2016-082

December 1, 2025 – filing 2025-077

NON-SUBSTANTIVE CORRECTIONS:

January 8, 2018 - Section 7(U) numbering corrected

AMENDED:

December 1, 2025 – filing 2025-232

APAO ACCESSIBILITY CHECK: December 11, 2025 (issues detected; however, attempts to fully resolve them would potentially substantively impact the rule)

APPENDIX A

ANALYTE MONITORING REQUIREMENTS

for

NEW WELL APPROVAL and

ROUTINE COMPLIANCE MONITORING

|  | MICROBIAL CONTAMINANTS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 40 CFR § 141.21 & 40CFR §§ 141.854-861 |  |  |  | Community System (C) |  |  |  | Non-Transient Non-Community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 3100 | Total Coliform Bacteria | NA | X |  | X |  | X |  | X | X | X | X | X |
|  | 3014 | Escherichia coli (E. coli) | NA | X |  | X |  | X |  | X | X | X | X | X |
|  | INORGANIC CONTAMINANTS |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.23 |  |  |  | Community System (C) |  |  |  | Non-Transient Non-Community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 1074 | Antimony | 7440-36-0 | X |  | X |  | X |  | X |  | X | X | X |
|  | 1005 | Arsenic | 7440-38-2 | X |  | X |  | X |  | X |  | X | X | X |
|  | 1094 | Asbestos | 1332-21-4 | X |  |  |  |  |  |  |  |  |  |  |
|  | 1010 | Barium | 7440-39-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1075 | Beryllium | 7440-41-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1015 | Cadmium | 7440-43-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1019 | Calcium | 7440-70-2 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1017 | Chloride | 16887-00-6 |  |  | X |  |  |  | X |  | X |  | X |
|  | 1020 | Chromium | 7440-47-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1905 | Color | NA |  |  | X |  |  |  | X |  |  |  | X |
|  | 1022 | Copper | 7440-50-8 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1024 | Cyanide (free CN-) | 57-12-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1025 | Fluoride | 16984-48-8 | X |  | X |  | X |  | X |  | X | X | X |
|  | 1915 | Hardness, Total (CaCO3) | NA |  |  | X |  |  |  | X |  | X |  | X |
|  | 1028 | Iron | 7439-89-6 |  |  | X |  |  |  | X |  | X |  | X |
|  | 1030 | Lead | 7439-92-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1031 | Magnesium | 7439-95-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1032 | Manganese | 7439-96-5 | X |  | X |  | X |  | X |  | X | X | X |
|  | 1035 | Mercury | 7439-97-6 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1036 | Nickel | 7440-02-0 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1040 | Nitrate | 14797-55-8 | X |  | X |  | X |  | X | X | X | X | X |
|  | 1041 | Nitrite | 14797-65-0 | X |  | X |  | X |  | X | X | X | X | X |
|  | 1925 | pH | NA |  |  | X |  |  |  | X |  | X |  | X |
|  | 1045 | Selenium | 7782-49-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 1050 | Silver | 7440-22-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1052 | Sodium | 7440-23-5 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1055 | Sulfate | 14808-79-8 |  |  | X |  |  |  | X |  |  |  | X |
|  | 1085 | Thallium | 7440-28-0 | X |  | X |  | X |  | X |  |  | X | X |
|  | 0100 | Turbidity | NA |  |  | X |  |  |  | X |  |  |  | X |
|  | 4006 | Uranium, Total | 7440-61-1 | X |  | X |  | X |  | X |  | X | X | X |
|  | 1095 | Zinc | 7440-66-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | RADIONUCLIDE CONTAMINANTS |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.25 (METHODS) & 40 CFR § 141.26 (MONITORING) |  |  |  | Community System (C) |  |  |  | Non-Transient Non-Community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 4000 | Gross alpha | NA | X |  | X |  |  |  | X |  |  | X | X |
|  | 4004 | Radon | 10043-92-2 | X |  | X |  |  |  | X |  |  | X | X |
|  | 4010 | Combined radium | NA | X |  |  |  |  |  |  |  |  | X |  |
|  | 4020 | Radium 226 | 7440-14-4 |  |  |  |  |  |  |  |  |  |  |  |
|  | 4030 | Radium 228 | 15262-20-1 |  |  |  |  |  |  |  |  |  |  |  |
|  | VOLATILE ORGANIC COMPOUND (VOC) CONTAMINANTS |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-Transient Non-Community System (NTNC) |  | Transient System (NC)** |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2981 | 1,1,1-Trichloroethane | 71-55-6 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2985 | 1,1,2-Trichloroethane | 79-00-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2977 | 1,1-Dichloroethylene | 75-35-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2378 | 1,2,4-Trichlorobenzene | 120-82-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2980 | 1,2-Dichloroethane | 107-06-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2983 | 1,2-Dichloropropane | 78-87-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2990 | Benzene | 71-43-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2982 | Carbon Tetrachloride | 56-23-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2989 | Chlorobenzene | 108-90-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2380 | Cis-1,2-Dichloroethylene | 156-59-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2964 | Dichloromethane | 75-09-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2992 | Ethylbenzene | 100-41-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2251 | Methyl Tert-Butyl Ether (MTBE) | 1634-04-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2968 | O-Dichlorobenzene | 95-50-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2969 | P-Dichlorobenzene | 106-46-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2996 | Styrene | 100-42-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2987 | Tetrachloroethylene | 127-18-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2991 | Toluene | 108-88-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2979 | Trans-1,2-Dichloroethylene | 156-60-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2984 | Trichloroethylene | 79-01-6 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2976 | Vinyl chloride | 75-01-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2955 | Xylenes, Total | 1330-20-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2986 | 1,1,1,2-Tetrachloroethane | 630-20-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2988 | 1,1,2,2- Tetrachloroethane | 79-34-5 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2978 | 1,1- Dichloroethane | 75-34-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2410 | 1,1-Dichloropropene | 563-58-6 |  |  | X |  |  |  | X |  |  |  | X |
| VOCs continued on next page. *MTBE is a State testing requirement. **Transient systems must test for VOCs at NWA if there is an underground storage tank (UST) within 1,000’ (feet) of the well. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | VOLATILE ORGANIC COMPOUND CONTAMINANTS (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-Transient Non-Community System (NTNC) |  | Transient System (NC)** |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2420 | 1,2,3-Trichlorobenzene | 87-61-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2414 | 1,2,3-Trichloropropane | 96-18-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2418 | 1,2,4-Trimethylbenzene | 95-63-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2424 | 1,3,5- Trimethylbenzene | 108-67-8 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2412 | 1,3-Dichloropropane | 142-28-9 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2413 | 1,3-Dichloropropene | 542-75-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2416 | 2,2- Dichloropropane | 594-20-7 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2993 | Bromobenzene | 108-86-1 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2430 | Bromochloromethane | 74-97-5 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2943 | Bromodichloromethane | 75-27-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2942 | Bromoform | 75-25-2 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2214 | Bromomethane | 74-83-9 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2216 | Chloroethane | 75-00-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2941 | Chloroform | 67-66-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2210 | Chloromethane | 74-87-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2944 | Dibromochloromethane | 124-48-1 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2408 | Dibromomethane | 74-95-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2246 | Hexachlorobutadiene | 87-68-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2967 | M-Dichlorobenzene | 541-73-1 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2248 | Naphthalene | 91-20-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2422 | N-Butylbenzene | 104-51-8 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2965 | O-Chlorotoluene | 95-49-8 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2966 | P- Chlorotoluene | 106-43-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2030 | P-Isopropyltoluene | 99-87-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2428 | Sec-Butylbenzene | 135-98-8 |  |  | X |  |  |  | X |  |  |  | X |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- SEMI-VOLATILE ORGANICS (SVO) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2050 | Atrazine | 1912-24-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2010 | BHC-Gamma | 58-89-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2035 | DI(2-Ethylhexyl) Adipate | 103-23-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2039 | DI(2-Ethylhexyl) Phthalate | 117-81-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2005 | Endrin | 72-20-8 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2065 | Heptachlor | 76-44-8 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2067 | Heptachlor epoxide | 1024-57-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2274 | Hexachlorobenzene | 118-74-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2042 | Hexachlorocyclopentadiene | 77-47-4 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2051 | Lasso | 15972-60-8 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2015 | Methoxychlor | 72-43-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2037 | Simazine | 122-34-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2076 | Butachlor | 23184-66-9 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2070 | Dieldrin | 60-57-1 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2045 | Metolachlor | 51218-45-2 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2077 | Propachlor | 1918-16-7 |  |  | X |  |  |  | X |  |  |  | X |
|  | *2012 | Velpar/Hexazinone | 51235-04-2 | X |  | X |  | X |  | X |  |  | X | X |
| *Velpar is a State of Maine Department testing requirement for systems with blueberry fields in the vicinity of the well. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- PESTICIDES-TOXAPHENE/CHLORDANE/PCB |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2959 | Chlordane | 57-74-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2383 | Total Polychlorinated Biphenyls (PCB) | 1336-36-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2388 | Aroclor 1016 | 12674-11-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2390 | Aroclor 1221 | 11104-28-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2392 | Aroclor 1232 | 11141-16-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2394 | Aroclor 1242 | 53469-21-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2396 | Aroclor 1248 | 12672-29-6 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2398 | Aroclor 1254 | 11097-69-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | *2400 | Aroclor 1260 | 11096-82-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2020 | Toxaphene | 8001-35-2 | X |  | X |  | X |  | X |  |  | X | X |
| *Only need to report individual results if there is a detect. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- HERBICIDES-CHLORINATED ACIDS |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2110 | 2,4,5-TP | 93-72-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2105 | 2,4-D | 94-75-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2031 | Dalapon | 75-99-0 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2041 | Dinoseb | 88-85-7 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2326 | Pentachlorophenol | 87-86-5 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2040 | Picloram | 1918-02-1 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2440 | Dicamba | 1918-00-9 |  |  | X |  |  |  | X |  |  |  | X |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- CARBAMATES |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2046 | Carbofuran | 1563-66-2 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2036 | Oxamyl | 23135-22-0 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2066 | 3-Hydroxycarbofuran | 16655-82-6 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2047 | Aldicarb | 116-06-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2044 | Aldicarb Sulfone | 1646-88-4 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2043 | Aldicarb Sulfoxide | 1646-87-3 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2021 | Carbaryl | 63-25-2 |  |  | X |  |  |  | X |  |  |  | X |
|  | 2022 | Methomyl | 16752-77-5 |  |  | X |  |  |  | X |  |  |  | X |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- OTHER |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40CFR § 141.24 |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# |  | Routine Compliance |  | NWA |  | Routine Compliance | NWA | Routine Compliance | NWA | Routine Compliance | NWA |  |
|  | 2032 | Diquat | 2764-72-9 | X |  | X |  | X |  | X |  |  | X | X |
|  | 2033 | Endothall | 145-73-3 | X |  | X |  | X |  | X |  |  | X | X |
|  | SYNTHETIC ORGANIC COMPOUND CONTAMINANTS- PFAS |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40 CFR §§ 141.900-905. |  |  |  | Community System (C) |  |  |  | Non-transient Non-community System (NTNC) |  | Transient System (NC) |  | Bottled Water Supplier (BW) |  |  |
| # | Analyte Code | Analyte | CAS# | Routine Compliance |  | NWA |  | Routine Compliance |  | NWA | Routine Compliance | NWA | Routine Compliance | NWA |
|  | 2830 | Total PFAS |  | X |  | X |  | X |  | X |  |  | X | X |
|  | 2801 | PFBS- Perfluorobutanesulfonate (2801-Perfluorobutanesulfonic acid) | 45187-15-3/ 375-73-5 |  | X |  | X |  | X | X |  |  | X | X |  |
|  | 2803 | PFHxS- Perfluorohexane sulfonate (2803- Perfluoro hexane sulfonic acid- 355-45-4) | 108427-53-8/ 355-45-4 |  | X |  | X |  | X | X |  |  | X | X |  |
|  | 2804 | PFNA- Perfluorononanoic acid | 72007-68-2/ 375-95-1 |  | X |  | X |  | X | X |  |  | X | X |  |
|  | 2805 | PFOS- Perfluorooctanesulfonate (2805-Perfluoroctane sulfonic acid- 1763-23-1) | 45298-90-6/ 1763-23-1 |  | X |  | X |  | X | X |  |  | X | X |  |
|  | 2806 | PFOA- Perfluorooctanoate (2806-perfluoroctanoic acid- 335-57-1) | 45285-51-6/ 335-57-1 |  | X |  | X |  | X | X |  |  | X | X |  |
|  | 2816 | HFPO-DA- 2,3,3,3-tetrafluoro-2-(heptafluoropropoxy) propanoate | 122499-17-6/ 13252-13-6 |  | X |  | X |  | X | X |  |  | X | X |  |

APPENDIX B

NATIONAL PRIMARY DRINKING WATER REGULATIONS CONTAMINANTS

MCL AND MCLG TABLE

| MICROBIAL CONTAMINANTS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Total Coliform | 0 | 40 CFR 141.63 | 0 | 40 CFR 141.52 |  |  |
|  | E. coli and fecal coliform | 0 | 40 CFR 141.63 | 0 | 40 CFR 141.52 |  |  |
|  | Heterotrophic plate count (HPC) | TT |  | N/A |  |  |  |
|  | Legionella | TT |  | 0 | 40 CFR 141.52 |  |  |
|  | Cryptosporidium | TT |  | 0 | 40 CFR 141.52 |  |  |
|  | Giardia lamblia | TT |  | 0 | 40 CFR 141.52 |  |  |
| INORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Antimony | 0.006 | 40 CFR 141.62 | 0.006 | 40 CFR 141.51 |  |  |
|  | Arsenic | 0.010 | 40 CFR 141.62 | 0 | 40 CFR 141.51 |  |  |
|  | Asbestos | 7 MFL | 40 CFR 141.62 | 7 MFL | 40 CFR 141.51 |  |  |
|  | Barium | 2.0 | 40 CFR 141.62 | 2.0 | 40 CFR 141.51 |  |  |
|  | Beryllium | 0.004 | 40 CFR 141.62 | 0.004 | 40 CFR 141.51 |  |  |
|  | Cadmium | 0.005 | 40 CFR 141.62 | 0.005 | 40 CFR 141.51 |  |  |
|  | Chloride |  |  |  |  | 250 (S) | EPA Secondary Standards |
|  | Chromium | 0.1 | 40 CFR 141.62 | 0.1 | 40 CFR 141.51 |  |  |
|  | Color |  |  |  |  | 15 CU (S) | EPA Secondary Standards |
|  | Copper | 1.3 AL | 40 CFR 141.62 | 1.3 | 40 CFR 141.51 | 1.0 (S) | EPA Secondary Standards |
|  | Cyanide (as free CN-) | 0.2 | 40 CFR 141.62 | 0.2 | 40 CFR 141.51 |  |  |
|  | Fluoride | 4.0 | 40 CFR 141.62 | 4.0 | 40 CFR 141.51 | 2.0 (S) | EPA Secondary Standards |
|  | Iron |  |  |  |  | 0.3 (S) | EPA Secondary Standards |
|  | Lead | 0.015 AL | 40 CFR 141.62 | 0 | 40 CFR 141.51 |  |  |
|  | Manganese |  |  |  |  | 0.05 (S) / 0.3 (HA) | EPA Secondary Standards |
|  | Mercury | 0.002 | 40 CFR 141.62 | 0.002 | 40 CFR 141.51 |  |  |
|  | Nitrate | 10 | 40 CFR 141.62 | 10 | 40 CFR 141.51 |  |  |
|  | Nitrite | 1 | 40 CFR 141.62 | 1 | 40 CFR 141.51 |  |  |
|  | pH |  |  |  |  | 6.5-8.5 (S) | EPA Secondary Standards |
|  | Selenium | 0.05 | 40 CFR 141.62 | 0.05 | 40 CFR 141.51 |  |  |
|  | Silver |  |  |  |  | 0.10 (S) | EPA Secondary Standards |
|  | Sodium |  |  |  |  | 20 (S) |  |
|  | Sulfate |  |  |  |  | 250 (S) | EPA Secondary Standards |
|  | Thallium | 0.002 | 40 CFR 141.62 | 0.0005 | 40 CFR 141.51 |  |  |
|  | Turbidity | 5 NTU | 40 CFR 141.62 |  |  |  |  |
|  | Zinc |  |  |  |  | 5 (S) | EPA Secondary Standards |
| RADIONUCLIDE CONTAMINANTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL pCi/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory pCi/L | Secondary Reference |
|  | Gross Alpha | 15 | 40 CFR 141.66 | 0 | 40 CFR 141.55 |  |  |
|  | Combined Radium | 5 | 40 CFR 141.66 | 0 | 40 CFR 141.55 |  |  |
|  | Uranium -238 | 0.03 mg/L | 40 CFR 141.66 | 0 | 40 CFR 141.55 |  |  |
|  | Radon |  |  |  |  | 4000 MEG | 10-144 CODE OF MAINE RULES CHAPTER 231 |
| ORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| VOLATILE ORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | 1,1,1-Trichloroethane | 0.2 | 40 CFR 141.61 | 0.2 | 40 CFR 141.50 |  |  |
|  | 1,1,2-Trichloroethane | 0.005 | 40 CFR 141.61 | 0.003 | 40 CFR 141.50 |  |  |
|  | 1,1-Dichloroethylene | 0.007 | 40 CFR 141.61 | 0.007 | 40 CFR 141.50 |  |  |
|  | 1,2,4-Trichlorobenzene | 0.07 | 40 CFR 141.61 | 0.07 | 40 CFR 141.50 |  |  |
|  | 1,2-Dichloroethane | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | 1,2-Dichloropropane | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | 1,2-Dichlorobenzene (o) | 0.6 | 40 CFR 141.61 | 0.6 | 40 CFR 141.50 |  |  |
|  | 1,4-Dichlorobenzene (p) | 0.075 | 40 CFR 141.61 | 0.075 | 40 CFR 141.50 |  |  |
|  | Benzene | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Carbon Tetrachloride | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Chlorobenzene | 0.1 | 40 CFR 141.61 | 0.1 | 40 CFR 141.50 |  |  |
|  | Cis-1,2-Dichloroethylene | 0.07 | 40 CFR 141.61 | 0.07 | 40 CFR 141.50 |  |  |
|  | Dichloromethane | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Ethylbenzene | 0.7 | 40 CFR 141.61 | 0.7 | 40 CFR 141.50 |  |  |
|  | Methyl Tert-Butyl Ether (MtBE) |  |  |  |  | 0.035 | 10-144 CODE OF MAINE RULES CHAPTER 231 |
|  | Styrene | 0.1 | 40 CFR 141.61 | 0.1 | 40 CFR 141.50 |  |  |
|  | Tetrachloroethylene | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Toluene | 1 | 40 CFR 141.61 | 1 | 40 CFR 141.50 |  |  |
|  | Trans-1,2-Dichloroethylene | 0.1 | 40 CFR 141.61 | 0.1 | 40 CFR 141.50 |  |  |
|  | Trichloroethylene | 0.005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Vinyl Chloride | 0.002 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Xylenes, Total | 10 | 40 CFR 141.61 | 10 | 40 CFR 141.50 |  |  |
| SYNTHETIC ORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| HERBICIDES |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | 2,4-D | 0.07 | 40 CFR 141.61 | 0.07 | 40 CFR 141.50 |  |  |
|  | 2,4,5-TP (Silvex) | 0.05 | 40 CFR 141.61 | 0.05 | 40 CFR 141.50 |  |  |
|  | Dalapon | 0.2 | 40 CFR 141.61 | 0.2 | 40 CFR 141.50 |  |  |
|  | Dinoseb | 0.007 | 40 CFR 141.61 | 0.007 | 40 CFR 141.50 |  |  |
|  | Pentachlorophenol | 0.001 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Picloram | 0.5 | 40 CFR 141.61 | 0.5 | 40 CFR 141.50 |  |  |
| CARBAMATES |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Carbofuran | 0.04 | 40 CFR 141.61 | 0.04 | 40 CFR 141.50 |  |  |
|  | Oxamyl (Vydate) | 0.2 | 40 CFR 141.61 | 0.2 | 40 CFR 141.50 |  |  |
| SEMI-VOLATILE ORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Atrazine | 0.003 | 40 CFR 141.61 | 0.003 | 40 CFR 141.50 |  |  |
|  | BHC-Gamma (Lindane) | 0.0002 | 40 CFR 141.61 | 0.0002 | 40 CFR 141.50 |  |  |
|  | Di(2-ethylhexyl) adipate | 0.4 | 40 CFR 141.61 | 0.4 | 40 CFR 141.50 |  |  |
|  | Di(2-ethylhexyl) phthalate | 0.006 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Endrin | 0.002 | 40 CFR 141.61 | 0.002 | 40 CFR 141.50 |  |  |
|  | Heptachlor | 0.0004 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Heptachlor epoxide | 0.0002 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
| SEMI-VOLATILE ORGANIC CONTAMINANTS (cont.) |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Hexachlorobenzene | 0.001 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Hexachlorocyclopentadiene | 0.05 | 40 CFR 141.61 | 0.05 | 40 CFR 141.50 |  |  |
|  | Alachlor (Lasso) | 0.002 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Methoxychlor | 0.04 | 40 CFR 141.61 | 0.04 | 40 CFR 141.50 |  |  |
|  | Simazine | 0.004 | 40 CFR 141.61 | 0.004 | 40 CFR 141.50 |  |  |
|  | Velpar/Hexazinone |  |  |  |  | 0.200 | 10-144 CODE OF MAINE RULES CHAPTER 231 |
| PESTICIDES |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Chlordane | 0.002 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | PCBs (Aroclors) | 0.0005 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
|  | Toxaphene | 0.003 | 40 CFR 141.61 | 0 | 40 CFR 141.50 |  |  |
| PER & POLY-FLUORO ALKYL SUBSTANCES (PFAS) |  |  |  |  |  |  |  |
| Row # | Analyte | MCL mg/L (unless otherwise noted) | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | HBWC (mg/L) for Hazard Index Calculation | Secondary Reference |
|  | PFOA | 0.0000040 | 40 CFR 141.61 | 0 | 40 CFR 141.50 | Not applicable |  |
|  | PFOS | 0.0000040 | 40 CFR 141.61 | 0 | 40 CFR 141.50 | Not applicable |  |
|  | HFPO-DA | 0.00001 | 40 CFR 141.61 |  |  | 0.00001 |  |
|  | PFBS | No individual MCL | 40 CFR 141.61 |  |  | 0.002 |  |
|  | PFHxS | 0.00001 | 40 CFR 141.61 |  |  | 0.00001 |  |
|  | PFNA | 0.00001 | 40 CFR 141.61 |  |  | 0.00001 |  |
|  | PFAS Hazard Index* | 1 (unitless) | 40 CFR 141.61 |  |  | Not applicable |  |
| OTHER SYNTHETIC ORGANIC CONTAMINANTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Diquat | 0.02 | 40 CFR 141.61 | 0.02 | 40 CFR 141.50 |  |  |
|  | Endothall | 0.1 | 40 CFR 141.61 | 0.1 | 40 CFR 141.50 |  |  |
| DISINFECTION BY-PRODUCTS |  |  |  |  |  |  |  |
| Row # | Analyte | MCL/AL mg/L | MCL CFR Reference | MCLG mg/L | MCLG CFR Reference | Secondary/Health Advisory mg/L | Secondary Reference |
|  | Haloacetic Acids | 0.060 | 40 CFR 141.64 | 0-0.07 | 40 CFR 141.53 |  |  |
|  | Total Trihalomethanes | 0.080 | 40 CFR 141.64 | 0-0.07 | 40 CFR 141.53 |  |  |

MCL=Maximum Contaminant Level

MCLGs=Maximum Contaminant Level Goal

AL=Action Level

HI=PFAS Mixture Hazard Index

HBWC=Health-Based Water Concentration

*The PFAS Mixture Hazard Index (HI) is the sum of component hazard quotients (HQs), which are calculated by dividing the measured component PFAS concentration in water by the relevant health-based water concentration when expressed in the same units (shown in ng/l for simplification).  The HBWC for PFHxS is 10 ng/l; the HBWC for HFPO-DA is 10 ng/l; the HBWC for PFNA is 10 ng/l; and the HBWC for PFBS is 2000 ng/l.

Hazard Index = ([HFPO-DAwater ng/l]/[10 ng/l]) + ([PFBSwater ng/l]/[2000 ng/l]) + ([PFNAwater ng/l]/[10 ng/l]) + ([PFHxSwater ng/l]/[10 ng/l])

HBWC = health-based water concentration

HQ = hazard quotient

ng/l = nanograms per liter

PFASwater = the concentration of a specific PFAS in water